## Sheet1
Water Treatment Industries Ltd.
Instrument Calibration Report
Section A :- General Calibration Report Number : 102
Plant :- Water Treatment Plant |  |  | Area :- Unit 1 |  |  |  | Tag No. :- 21-TS-0101 |  | Date :- 30 Nov 2023
Instrument Make : Barksdale |  |  |  |  | Instrument Model Number: ML1H
Order number :- 6542761221 |  |  | Type of Instrument :- Temperature Switch |  |  |  |  | Work Permit No. :- 459690
Trip Bypassed :- Interlock not applicable as plant S/D |  |  | Trip Bypass Restored :- Not Applicable |  |  |  |  | Calibration Job By :- Person 1
Interlock Bypass Form Number :- Not Applicable |  |  | Interlock Bypass Approvers :- Not Applicable
Section B :- Calibration Job Readings | [7 empty] | InstrumentationTools.com
Set point :- 100 deg C |  |  |  |  | Accuracy as per Datasheet :- (+/- %) 2 %
|  |  | Reading Before Adjustment |  |  |  | Reading After Adjustment
Sr No. | Set Value | Contact Use | Increasing | Decreasing | Hysteresis | Error % | Increasing | Decreasing | Hysteresis | Error % | Status
1 | 100 | NC | 99 | 96 | 3 | 1 |  |  |  |  | OK
2 | 100 | NC | 99.5 | 96 | 3.5 | 0.5 |  |  |  |  | OK
3 | 100 | NC | 99 | 96.5 | 2.5 | 1 |  |  |  |  | OK
4 | 100 | NC | 99.5 | 96 | 3.5 | 0.5 |  |  |  |  | OK
5 | 100 | NC | 100 | 96.5 | 3.5 | 0 |  |  |  |  | OK
Maximum Error is 1 %. Hence this temperature switch is OK
Section C :- Details of all Calibration Instruments used for the Job
Type of inst. |  | Inst. Sr No. | Make |  | Model |  |  | Range | Valid Upto
Digital Multimeter |  | 735214 | Fluke |  | 87V |  |  | 0 mA to 300 mA | 2024-03-31 |  | 44716
Temperature Bath |  | 768785 | Wika |  | CTM9100-150 |  |  | (-20) deg C to 150 deg C | 2024-03-31 |  | 44716
Reference RTD |  | 785214 | Omega |  | PT100 |  |  | (-200) deg C to 600 deg C | 2024-03-31 |  | 44716
Remarks : Reference RTD used for cross verifying temperature. Minor coating is observed on the temperature switch's element. Element is OK as per response.
Section D :- PM Validation
Job Done By:- |  |  |  |  | Verified By Instrument Engineer :-
Name |  |  | Sign | Date | Name |  |  |  | Sign |  | Date
Person 1 |  |  |  | 2023-11-30 | Instrument Engineer 1 | [5 empty] | 2023-11-30
Formulas:
Status = [Decreasing]