## Instructions
PID CONTROLLER SIMULATOR
This worksheet simulate a simple level control in a tank. The algoritm PID, for discrete values, is used to simulate the process:
Where:
-
-
-
-
-
-
-
It was cosidered that the controller has in input (Cin) and in output (CO) the variables according to the standard 4-20 mA.
Sampling time ∆t is equal to 1 s. The system is initially in a steady state with settable input flow rate equal to output flowrate (refer to sheet "Calculation", cell J21).
At t = 0 it takes a step disturbance on the discharge line by means of the pump (refer to sheet "Calculation", cell J24)
Through mass balance the actual level (Present Value) is calculated (refer to sheet "Calculation", cells C44:C2116). Obviously in real case there is a Level Trasmitter that "read" and communicate at the controller the PV.
It is possible to put in the system a dead time (refer to sheet "Calculation", cell J25) just to see the effect on the PID controller.
The algoritm PID determines the control action on the control valve that modify the inlet flowrate.
The control valve has a linear characteristic: Fin= % opening valve / 100 * Fmax, in.
To disable the derivative action is sufficient to set Td = 0 (refer to sheet "Calculation", cell J8) while to disable the integral action set value 0 in the cell J9, sheet "Calculation".
Note: this excel file simulates an "academic" version of the PID controller.
〖𝑪𝑶〗_𝒏= 𝑲_𝒑∗𝑬_𝒏+𝑲_𝒑 𝚫𝒕/𝑻_𝑰 ∑_(𝒊=𝟎)^(𝒊=𝒏)▒〖𝑬_𝒊+𝑲_𝒑 𝑻_𝑫/𝚫𝒕 (𝑬_𝒏−𝑬_(𝒏−𝟏) )+〖𝑪𝑶〗_𝟎 〗
, mA
〖𝐶𝑂〗_(𝑛 ):𝑐𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑟 𝑜𝑢𝑡𝑝𝑢𝑡 𝑠𝑖𝑔𝑛𝑎𝑙 𝑎𝑡 𝑛−𝑡ℎ 𝑠𝑎𝑚𝑝𝑙𝑒, mA
, mA
𝐸_(𝑛 ):𝑒𝑟𝑟𝑜𝑟 𝑎𝑡 𝑛−𝑡ℎ 𝑠𝑎𝑚𝑝𝑙𝑒, mA
, s
∆𝑡:𝑠𝑎𝑚𝑝𝑙𝑖𝑛𝑔 𝑡𝑖𝑚𝑒, s
𝐾_𝑝:𝑝𝑟𝑜𝑝𝑜𝑟𝑡𝑖𝑜𝑛𝑎𝑙 𝑎𝑐𝑡𝑖𝑜𝑛 𝑐𝑜𝑠𝑡𝑎𝑛𝑡
, s
𝑇_𝐼:𝑖𝑛𝑡𝑒𝑔𝑟𝑎𝑙 𝑎𝑐𝑡𝑖𝑜𝑛 𝑡𝑖𝑚𝑒, s
,s
𝑇_𝐷:𝑑𝑒𝑟𝑖𝑣𝑎𝑡𝑒 𝑎𝑐𝑡𝑖𝑜𝑛 𝑡𝑖𝑚𝑒,s
(t=0), mA
〖𝐶𝑂〗_0:𝑐𝑜𝑛𝑡𝑟𝑜𝑙𝑙𝑒𝑟 𝑜𝑢𝑡𝑝𝑢𝑡 𝑠𝑖𝑔𝑛𝑎𝑙 𝑎𝑡 𝑖𝑛𝑖𝑡𝑖𝑎𝑙 𝑠𝑡𝑒𝑎𝑑𝑦 𝑠𝑡𝑎𝑡𝑒 (t=0), mA

## Calculation
INPUT DATA
[9 empty] | PID |  |  |  |  | OUTPUT DATA
[8 empty] | KP | 3
[8 empty] | TI, s | 60
[8 empty] | TD, s | 1
[7 empty] | Integral on(1)/off(0) |  | 1 |  |  |  |  | Direct | ------------> | E = PV - SP | If PV > SP then CO (controller output signal) increase
[7 empty] | Opening valve t=0,% |  | 0 |  |  |  |  | Indirect | ------------> | E = SP - PV | If PV > SP then CO (controller output signal) decrease
[7 empty] | Controller action |  | Indirect
[7 empty] | Control valve |  | Fail close |  |  |  |  | Fail close | ------------> | Air to open
[7 empty] | F max in, mc/h |  | 50 |  |  |  |  | Fail open | ------------> | Air to close
[7 empty] | Level min, m |  | 0
[7 empty] | Level max, m |  | 5
[7 empty] | Set Point (SP), m |  | 2
[7 empty] | Fout=Fin at t=0, mc/h |  | 0
[7 empty] | Diameter, m | Diametro, m | 2.5
[7 empty] | Section, m2 |  | 4.9062
[7 empty] | Disturbance, mc/h |  | 20
[7 empty] | Dead time, s |  | 0
DO NOT TOUCH BELOW VALUES
P | FALSE
PD | FALSE
PI | FALSE
PID
Controller PID - SP = 2 m - Kp = 3 - Ti = 60 s - Td = 1 s
[8 empty] | Error |  |  | Proportional action | Integral action | Derivative action | PID | [5 empty] | It is only used to calculate the PV; in real case PV comes from Level Transmitter
∆t = 1s | [15 empty] | CO, mA | 4 < CO < 20 | CO corr, mA | % vlv |  |  |  |  | Sum
t, s | t, min | PV, m | Cin, mA | SP, m | C sp, mA | % vlv | Vlv at t=0,% | 0 | 0 | 0 | [9 empty] | Fin, mc/h | D, mc/h | Fout, mc/h | Fin - Fus | 0
0 | 0 | 2 | 10.4 | 2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 4 | 4 | 0 | 0 | 20 | 20 | -20 | -20
1 | 0.016667 | 1.9959 | 10.387 | 2 | 10.4 | 0.49325 | 0 | 0.013045 | 0.013045 | 0.013045 | 0.039134 | 0.00065223 | 0.039134 | 0.07892 |  | 4.0789 | 4 | 4.0789 | 0.49325 | 0.24662 | 20 | 20 | -19.7534 | -39.7534
2 | 0.033333 | 1.9919 | 10.3741 | 2 | 10.4 | 0.7399 | 0 | 0.025928 | 0.038973 | 0.012884 | 0.077785 | 0.0019486 | 0.038651 | 0.11838 |  | 4.1184 | 4 | 4.1184 | 0.7399 | 0.36995 | 20 | 20 | -19.63 | -59.3834
3 | 0.05 | 1.9879 | 10.3613 | 2 | 10.4 | 0.99056 | 0 | 0.038732 | 0.077705 | 0.012803 | 0.11619 | 0.0038852 | 0.03841 | 0.15849 |  | 4.1585 | 4 | 4.1585 | 0.99056 | 0.49528 | 20 | 20 | -19.5047 | -78.8881
4 | 0.066667 | 1.9839 | 10.3485 | 2 | 10.4 | 1.2436 | 0 | 0.051453 | 0.12916 | 0.012722 | 0.15436 | 0.0064579 | 0.038165 | 0.19898 |  | 4.199 | 4 | 4.199 | 1.2436 | 0.62182 | 20 | 20 | -19.3782 | -98.2663
5 | 0.083333 | 1.98 | 10.3359 | 2 | 10.4 | 1.4991 | 0 | 0.064092 | 0.19325 | 0.012639 | 0.19228 | 0.0096625 | 0.037917 | 0.23986 |  | 4.2399 | 4 | 4.2399 | 1.4991 | 0.74955 | 20 | 20 | -19.2504 | -117.5168
6 | 0.1 | 1.976 | 10.3234 | 2 | 10.4 | 1.7569 | 0 | 0.076648 | 0.2699 | 0.012556 | 0.22994 | 0.013495 | 0.037667 | 0.28111 |  | 4.2811 | 4 | 4.2811 | 1.7569 | 0.87846 | 20 | 20 | -19.1215 | -136.6383
7 | 0.11667 | 1.9722 | 10.3109 | 2 | 10.4 | 2.017 | 0 | 0.08912 | 0.35902 | 0.012472 | 0.26736 | 0.017951 | 0.037415 | 0.32272 |  | 4.3227 | 4 | 4.3227 | 2.017 | 1.0085 | 20 | 20 | -18.9915 | -155.6298
8 | 0.13333 | 1.9683 | 10.2985 | 2 | 10.4 | 2.2794 | 0 | 0.10151 | 0.46052 | 0.012387 | 0.30452 | 0.023026 | 0.03716 | 0.36471 |  | 4.3647 | 4 | 4.3647 | 2.2794 | 1.1397 | 20 | 20 | -18.8603 | -174.4901
9 | 0.15 | 1.9644 | 10.2862 | 2 | 10.4 | 2.544 | 0 | 0.11381 | 0.57433 | 0.012301 | 0.34142 | 0.028717 | 0.036904 | 0.40704 |  | 4.407 | 4 | 4.407 | 2.544 | 1.272 | 20 | 20 | -18.728 | -193.2181
10 | 0.16667 | 1.9606 | 10.274 | 2 | 10.4 | 2.8108 | 0 | 0.12602 | 0.70035 | 0.012215 | 0.37807 | 0.035018 | 0.036645 | 0.44973 |  | 4.4497 | 4 | 4.4497 | 2.8108 | 1.4054 | 20 | 20 | -18.5946 | -211.8127
11 | 0.18333 | 1.9568 | 10.2618 | 2 | 10.4 | 3.0798 | 0 | 0.13815 | 0.8385 | 0.012128 | 0.41445 | 0.041925 | 0.036384 | 0.49276 |  | 4.4928 | 4 | 4.4928 | 3.0798 | 1.5399 | 20 | 20 | -18.4601 | -230.2728
12 | 0.2 | 1.9531 | 10.2498 | 2 | 10.4 | 3.3508 | 0 | 0.15019 | 0.98869 | 0.01204 | 0.45057 | 0.049435 | 0.036121 | 0.53613 |  | 4.5361 | 4 | 4.5361 | 3.3508 | 1.6754 | 20 | 20 | -18.3246 | -248.5974
13 | 0.21667 | 1.9493 | 10.2379 | 2 | 10.4 | 3.6239 | 0 | 0.16214 | 1.1508 | 0.011952 | 0.48643 | 0.057542 | 0.035856 | 0.57982 |  | 4.5798 | 4 | 4.5798 | 3.6239 | 1.812 | 20 | 20 | -18.188 | -266.7855
14 | 0.23333 | 1.9456 | 10.226 | 2 | 10.4 | 3.899 | 0 | 0.17401 | 1.3248 | 0.011863 | 0.52202 | 0.066242 | 0.035588 | 0.62385 |  | 4.6238 | 4 | 4.6238 | 3.899 | 1.9495 | 20 | 20 | -18.0505 | -284.8359
15 | 0.25 | 1.9419 | 10.2142 | 2 | 10.4 | 4.1762 | 0 | 0.18578 | 1.5106 | 0.011773 | 0.55734 | 0.075531 | 0.035319 | 0.66819 |  | 4.6682 | 4 | 4.6682 | 4.1762 | 2.0881 | 20 | 20 | -17.9119 | -302.7479
16 | 0.26667 | 1.9383 | 10.2025 | 2 | 10.4 | 4.4552 | 0 | 0.19746 | 1.7081 | 0.011683 | 0.59238 | 0.085404 | 0.035048 | 0.71284 |  | 4.7128 | 4 | 4.7128 | 4.4552 | 2.2276 | 20 | 20 | -17.7724 | -320.5202
17 | 0.28333 | 1.9347 | 10.1909 | 2 | 10.4 | 4.7362 | 0 | 0.20905 | 1.9171 | 0.011592 | 0.62716 | 0.095857 | 0.034775 | 0.75779 |  | 4.7578 | 4 | 4.7578 | 4.7362 | 2.3681 | 20 | 20 | -17.6319 | -338.1522
18 | 0.3 | 1.9311 | 10.1794 | 2 | 10.4 | 5.019 | 0 | 0.22055 | 2.1377 | 0.0115 | 0.66166 | 0.10688 | 0.0345 | 0.80304 |  | 4.803 | 4 | 4.803 | 5.019 | 2.5095 | 20 | 20 | -17.4905 | -355.6426
19 | 0.31667 | 1.9275 | 10.168 | 2 | 10.4 | 5.3037 | 0 | 0.23196 | 2.3696 | 0.011408 | 0.69588 | 0.11848 | 0.034223 | 0.84859 |  | 4.8486 | 4 | 4.8486 | 5.3037 | 2.6518 | 20 | 20 | -17.3482 | -372.9908
20 | 0.33333 | 1.924 | 10.1567 | 2 | 10.4 | 5.5901 | 0 | 0.24328 | 2.6129 | 0.011315 | 0.72983 | 0.13065 | 0.033945 | 0.89442 |  | 4.8944 | 4 | 4.8944 | 5.5901 | 2.7951 | 20 | 20 | -17.2049 | -390.1958
21 | 0.35 | 1.9205 | 10.1455 | 2 | 10.4 | 5.8783 | 0 | 0.2545 | 2.8674 | 0.011222 | 0.76349 | 0.14337 | 0.033665 | 0.94053 |  | 4.9405 | 4 | 4.9405 | 5.8783 | 2.9391 | 20 | 20 | -17.0609 | -407.2566
22 | 0.36667 | 1.917 | 10.1344 | 2 | 10.4 | 6.1682 | 0 | 0.26562 | 3.133 | 0.011128 | 0.79687 | 0.15665 | 0.033383 | 0.98691 |  | 4.9869 | 4 | 4.9869 | 6.1682 | 3.0841 | 20 | 20 | -16.9159 | -424.1725
23 | 0.38333 | 1.9135 | 10.1233 | 2 | 10.4 | 6.4597 | 0 | 0.27666 | 3.4097 | 0.011033 | 0.82997 | 0.17049 | 0.033099 | 1.0336 |  | 5.0336 | 4 | 5.0336 | 6.4597 | 3.2299 | 20 | 20 | -16.7701 | -440.9427
24 | 0.4 | 1.9101 | 10.1124 | 2 | 10.4 | 6.7529 | 0 | 0.2876 | 3.6973 | 0.010938 | 0.86279 | 0.18486 | 0.032814 | 1.0805 |  | 5.0805 | 4 | 5.0805 | 6.7529 | 3.3765 | 20 | 20 | -16.6235 | -457.5662
25 | 0.41667 | 1.9067 | 10.1016 | 2 | 10.4 | 7.0477 | 0 | 0.29844 | 3.9957 | 0.010842 | 0.89531 | 0.19979 | 0.032527 | 1.1276 |  | 5.1276 | 4 | 5.1276 | 7.0477 | 3.5238 | 20 | 20 | -16.4762 | -474.0424
26 | 0.43333 | 1.9034 | 10.0908 | 2 | 10.4 | 7.344 | 0 | 0.30918 | 4.3049 | 0.010746 | 0.92755 | 0.21525 | 0.032239 | 1.175 |  | 5.175 | 4 | 5.175 | 7.344 | 3.672 | 20 | 20 | -16.328 | -490.3704
27 | 0.45 | 1.9001 | 10.0802 | 2 | 10.4 | 7.6418 | 0 | 0.31983 | 4.6248 | 0.01065 | 0.9595 | 0.23124 | 0.031949 | 1.2227 |  | 5.2227 | 4 | 5.2227 | 7.6418 | 3.8209 | 20 | 20 | -16.1791 | -506.5495
28 | 0.46667 | 1.8968 | 10.0696 | 2 | 10.4 | 7.9411 | 0 | 0.33039 | 4.9551 | 0.010552 | 0.99116 | 0.24776 | 0.031657 | 1.2706 |  | 5.2706 | 4 | 5.2706 | 7.9411 | 3.9705 | 20 | 20 | -16.0295 | -522.5789
29 | 0.48333 | 1.8935 | 10.0592 | 2 | 10.4 | 8.2418 | 0 | 0.34084 | 5.296 | 0.010455 | 1.0225 | 0.2648 | 0.031365 | 1.3187 |  | 5.3187 | 4 | 5.3187 | 8.2418 | 4.1209 | 20 | 20 | -15.8791 | -538.458
30 | 0.5 | 1.8903 | 10.0488 | 2 | 10.4 | 8.5439 | 0 | 0.3512 | 5.6472 | 0.010357 | 1.0536 | 0.28236 | 0.03107 | 1.367 |  | 5.367 | 4 | 5.367 | 8.5439 | 4.2719 | 20 | 20 | -15.7281 | -554.1861
31 | 0.51667 | 1.887 | 10.0385 | 2 | 10.4 | 8.8473 | 0 | 0.36146 | 6.0086 | 0.010258 | 1.0844 | 0.30043 | 0.030775 | 1.4156 |  | 5.4156 | 4 | 5.4156 | 8.8473 | 4.4237 | 20 | 20 | -15.5763 | -569.7624
32 | 0.53333 | 1.8839 | 10.0284 | 2 | 10.4 | 9.1521 | 0 | 0.37162 | 6.3803 | 0.010159 | 1.1148 | 0.31901 | 0.030478 | 1.4643 |  | 5.4643 | 4 | 5.4643 | 9.1521 | 4.5761 | 20 | 20 | -15.4239 | -585.1863
33 | 0.55 | 1.8807 | 10.0183 | 2 | 10.4 | 9.4581 | 0 | 0.38168 | 6.7619 | 0.01006 | 1.145 | 0.3381 | 0.03018 | 1.5133 |  | 5.5133 | 4 | 5.5133 | 9.4581 | 4.7291 | 20 | 20 | -15.2709 | -600.4573
34 | 0.56667 | 1.8776 | 10.0084 | 2 | 10.4 | 9.7654 | 0 | 0.39164 | 7.1536 | 0.0099601 | 1.1749 | 0.35768 | 0.02988 | 1.5625 |  | 5.5625 | 4 | 5.5625 | 9.7654 | 4.8827 | 20 | 20 | -15.1173 | -615.5746
35 | 0.58333 | 1.8745 | 9.9985 | 2 | 10.4 | 10.0739 | 0 | 0.4015 | 7.5551 | 0.0098599 | 1.2045 | 0.37775 | 0.02958 | 1.6118 |  | 5.6118 | 4 | 5.6118 | 10.0739 | 5.0369 | 20 | 20 | -14.9631 | -630.5376
36 | 0.6 | 1.8715 | 9.9887 | 2 | 10.4 | 10.3835 | 0 | 0.41126 | 7.9663 | 0.0097593 | 1.2338 | 0.39832 | 0.029278 | 1.6614 |  | 5.6614 | 4 | 5.6614 | 10.3835 | 5.1917 | 20 | 20 | -14.8083 | -645.3459
37 | 0.61667 | 1.8685 | 9.9791 | 2 | 10.4 | 10.6942 | 0 | 0.42091 | 8.3872 | 0.0096584 | 1.2627 | 0.41936 | 0.028975 | 1.7111 |  | 5.7111 | 4 | 5.7111 | 10.6942 | 5.3471 | 20 | 20 | -14.6529 | -659.9988
38 | 0.63333 | 1.8655 | 9.9695 | 2 | 10.4 | 11.006 | 0 | 0.43047 | 8.8177 | 0.009557 | 1.2914 | 0.44088 | 0.028671 | 1.761 |  | 5.761 | 4 | 5.761 | 11.006 | 5.503 | 20 | 20 | -14.497 | -674.4957
39 | 0.65 | 1.8625 | 9.9601 | 2 | 10.4 | 11.3189 | 0 | 0.43993 | 9.2576 | 0.0094554 | 1.3198 | 0.46288 | 0.028366 | 1.811 |  | 5.811 | 4 | 5.811 | 11.3189 | 5.6595 | 20 | 20 | -14.3405 | -688.8363
40 | 0.66667 | 1.8596 | 9.9507 | 2 | 10.4 | 11.6328 | 0 | 0.44928 | 9.7069 | 0.0093533 | 1.3478 | 0.48535 | 0.02806 | 1.8612 |  | 5.8612 | 4 | 5.8612 | 11.6328 | 5.8164 | 20 | 20 | -14.1836 | -703.0199
41 | 0.68333 | 1.8567 | 9.9415 | 2 | 10.4 | 11.9476 | 0 | 0.45853 | 10.1654 | 0.009251 | 1.3756 | 0.50827 | 0.027753 | 1.9116 |  | 5.9116 | 4 | 5.9116 | 11.9476 | 5.9738 | 20 | 20 | -14.0262 | -717.0461
42 | 0.7 | 1.8539 | 9.9323 | 2 | 10.4 | 12.2633 | 0 | 0.46768 | 10.6331 | 0.0091483 | 1.403 | 0.53166 | 0.027445 | 1.9621 |  | 5.9621 | 4 | 5.9621 | 12.2633 | 6.1317 | 20 | 20 | -13.8683 | -730.9144
43 | 0.71667 | 1.851 | 9.9233 | 2 | 10.4 | 12.58 | 0 | 0.47672 | 11.1098 | 0.0090453 | 1.4302 | 0.55549 | 0.027136 | 2.0128 |  | 6.0128 | 4 | 6.0128 | 12.58 | 6.29 | 20 | 20 | -13.71 | -744.6244
44 | 0.73333 | 1.8482 | 9.9143 | 2 | 10.4 | 12.8975 | 0 | 0.48567 | 11.5955 | 0.0089421 | 1.457 | 0.57978 | 0.026826 | 2.0636 |  | 6.0636 | 4 | 6.0636 | 12.8975 | 6.4487 | 20 | 20 | -13.5513 | -758.1757
45 | 0.75 | 1.8455 | 9.9055 | 2 | 10.4 | 13.2158 | 0 | 0.4945 | 12.09 | 0.0088385 | 1.4835 | 0.6045 | 0.026516 | 2.1145 |  | 6.1145 | 4 | 6.1145 | 13.2158 | 6.6079 | 20 | 20 | -13.3921 | -771.5678
46 | 0.76667 | 1.8427 | 9.8968 | 2 | 10.4 | 13.5349 | 0 | 0.50324 | 12.5932 | 0.0087347 | 1.5097 | 0.62966 | 0.026204 | 2.1656 |  | 6.1656 | 4 | 6.1656 | 13.5349 | 6.7674 | 20 | 20 | -13.2326 | -784.8003
47 | 0.78333 | 1.84 | 9.8881 | 2 | 10.4 | 13.8547 | 0 | 0.51187 | 13.1051 | 0.0086307 | 1.5356 | 0.65526 | 0.025892 | 2.2168 |  | 6.2168 | 4 | 6.2168 | 13.8547 | 6.9274 | 20 | 20 | -13.0726 | -797.873
48 | 0.8 | 1.8374 | 9.8796 | 2 | 10.4 | 14.1753 | 0 | 0.5204 | 13.6255 | 0.0085264 | 1.5612 | 0.68128 | 0.025579 | 2.268 |  | 6.268 | 4 | 6.268 | 14.1753 | 7.0876 | 20 | 20 | -12.9124 | -810.7853
49 | 0.81667 | 1.8347 | 9.8712 | 2 | 10.4 | 14.4965 | 0 | 0.52882 | 14.1543 | 0.0084218 | 1.5865 | 0.70772 | 0.025265 | 2.3194 |  | 6.3194 | 4 | 6.3194 | 14.4965 | 7.2482 | 20 | 20 | -12.7518 | -823.5371
50 | 0.83333 | 1.8321 | 9.8629 | 2 | 10.4 | 14.8183 | 0 | 0.53714 | 14.6915 | 0.0083171 | 1.6114 | 0.73457 | 0.024951 | 2.3709 |  | 6.3709 | 4 | 6.3709 | 14.8183 | 7.4092 | 20 | 20 | -12.5908 | -836.1279
51 | 0.85 | 1.8296 | 9.8547 | 2 | 10.4 | 15.1407 | 0 | 0.54535 | 15.2368 | 0.0082121 | 1.636 | 0.76184 | 0.024636 | 2.4225 |  | 6.4225 | 4 | 6.4225 | 15.1407 | 7.5704 | 20 | 20 | -12.4296 | -848.5576
52 | 0.86667 | 1.827 | 9.8465 | 2 | 10.4 | 15.4637 | 0 | 0.55345 | 15.7903 | 0.008107 | 1.6604 | 0.78951 | 0.024321 | 2.4742 |  | 6.4742 | 4 | 6.4742 | 15.4637 | 7.7319 | 20 | 20 | -12.2681 | -860.8257
53 | 0.88333 | 1.8245 | 9.8385 | 2 | 10.4 | 15.7872 | 0 | 0.56146 | 16.3517 | 0.0080016 | 1.6844 | 0.81759 | 0.024005 | 2.526 |  | 6.526 | 4 | 6.526 | 15.7872 | 7.8936 | 20 | 20 | -12.1064 | -872.9321
54 | 0.9 | 1.8221 | 9.8306 | 2 | 10.4 | 16.1112 | 0 | 0.56935 | 16.9211 | 0.0078961 | 1.7081 | 0.84605 | 0.023688 | 2.5778 |  | 6.5778 | 4 | 6.5778 | 16.1112 | 8.0556 | 20 | 20 | -11.9444 | -884.8765
55 | 0.91667 | 1.8196 | 9.8229 | 2 | 10.4 | 16.4357 | 0 | 0.57714 | 17.4982 | 0.0077905 | 1.7314 | 0.87491 | 0.023371 | 2.6297 |  | 6.6297 | 4 | 6.6297 | 16.4357 | 8.2178 | 20 | 20 | -11.7822 | -896.6586
56 | 0.93333 | 1.8172 | 9.8152 | 2 | 10.4 | 16.7605 | 0 | 0.58483 | 18.083 | 0.0076847 | 1.7545 | 0.90415 | 0.023054 | 2.6817 |  | 6.6817 | 4 | 6.6817 | 16.7605 | 8.3803 | 20 | 20 | -11.6197 | -908.2784
57 | 0.95 | 1.8149 | 9.8076 | 2 | 10.4 | 17.0858 | 0 | 0.59241 | 18.6754 | 0.0075787 | 1.7772 | 0.93377 | 0.022736 | 2.7337 |  | 6.7337 | 4 | 6.7337 | 17.0858 | 8.5429 | 20 | 20 | -11.4571 | -919.7355
58 | 0.96667 | 1.8125 | 9.8001 | 2 | 10.4 | 17.4114 | 0 | 0.59988 | 19.2753 | 0.0074727 | 1.7996 | 0.96377 | 0.022418 | 2.7858 |  | 6.7858 | 4 | 6.7858 | 17.4114 | 8.7057 | 20 | 20 | -11.2943 | -931.0298
59 | 0.98333 | 1.8102 | 9.7928 | 2 | 10.4 | 17.7373 | 0 | 0.60724 | 19.8826 | 0.0073665 | 1.8217 | 0.99413 | 0.022099 | 2.838 |  | 6.838 | 4 | 6.838 | 17.7373 | 8.8686 | 20 | 20 | -11.1314 | -942.1611
60 | 1 | 1.808 | 9.7855 | 2 | 10.4 | 18.0634 | 0 | 0.61451 | 20.4971 | 0.0072602 | 1.8435 | 1.0249 | 0.021781 | 2.8901 |  | 6.8901 | 4 | 6.8901 | 18.0634 | 9.0317 | 20 | 20 | -10.9683 | -953.1294
61 | 1.0167 | 1.8057 | 9.7783 | 2 | 10.4 | 18.3898 | 0 | 0.62166 | 21.1187 | 0.0071538 | 1.865 | 1.0559 | 0.021462 | 2.9424 |  | 6.9424 | 4 | 6.9424 | 18.3898 | 9.1949 | 20 | 20 | -10.8051 | -963.9345
62 | 1.0333 | 1.8035 | 9.7713 | 2 | 10.4 | 18.7165 | 0 | 0.62871 | 21.7474 | 0.0070474 | 1.8861 | 1.0874 | 0.021142 | 2.9946 |  | 6.9946 | 4 | 6.9946 | 18.7165 | 9.3582 | 20 | 20 | -10.6418 | -974.5763
63 | 1.05 | 1.8014 | 9.7644 | 2 | 10.4 | 19.0432 | 0 | 0.63565 | 22.3831 | 0.0069409 | 1.9069 | 1.1192 | 0.020823 | 3.0469 |  | 7.0469 | 4 | 7.0469 | 19.0432 | 9.5216 | 20 | 20 | -10.4784 | -985.0546
64 | 1.0667 | 1.7992 | 9.7575 | 2 | 10.4 | 19.3702 | 0 | 0.64248 | 23.0256 | 0.0068343 | 1.9274 | 1.1513 | 0.020503 | 3.0992 |  | 7.0992 | 4 | 7.0992 | 19.3702 | 9.6851 | 20 | 20 | -10.3149 | -995.3696
65 | 1.0833 | 1.7971 | 9.7508 | 2 | 10.4 | 19.6972 | 0 | 0.64921 | 23.6748 | 0.0067277 | 1.9476 | 1.1837 | 0.020183 | 3.1515 |  | 7.1515 | 4 | 7.1515 | 19.6972 | 9.8486 | 20 | 20 | -10.1514 | -1005.521
66 | 1.1 | 1.7951 | 9.7442 | 2 | 10.4 | 20.0243 | 0 | 0.65583 | 24.3306 | 0.006621 | 1.9675 | 1.2165 | 0.019863 | 3.2039 |  | 7.2039 | 4 | 7.2039 | 20.0243 | 10.0121 | 20 | 20 | -9.9879 | -1015.5088
67 | 1.1167 | 1.793 | 9.7377 | 2 | 10.4 | 20.3514 | 0 | 0.66234 | 24.993 | 0.0065144 | 1.987 | 1.2496 | 0.019543 | 3.2562 |  | 7.2562 | 4 | 7.2562 | 20.3514 | 10.1757 | 20 | 20 | -9.8243 | -1025.3331
68 | 1.1333 | 1.791 | 9.7312 | 2 | 10.4 | 20.6785 | 0 | 0.66875 | 25.6617 | 0.0064077 | 2.0063 | 1.2831 | 0.019223 | 3.3086 |  | 7.3086 | 4 | 7.3086 | 20.6785 | 10.3393 | 20 | 20 | -9.6607 | -1034.9939
69 | 1.15 | 1.789 | 9.7249 | 2 | 10.4 | 21.0056 | 0 | 0.67505 | 26.3368 | 0.006301 | 2.0252 | 1.3168 | 0.018903 | 3.3609 |  | 7.3609 | 4 | 7.3609 | 21.0056 | 10.5028 | 20 | 20 | -9.4972 | -1044.4911
70 | 1.1667 | 1.7871 | 9.7188 | 2 | 10.4 | 21.3327 | 0 | 0.68125 | 27.018 | 0.0061943 | 2.0437 | 1.3509 | 0.018583 | 3.4132 |  | 7.4132 | 4 | 7.4132 | 21.3327 | 10.6663 | 20 | 20 | -9.3337 | -1053.8247
71 | 1.1833 | 1.7852 | 9.7127 | 2 | 10.4 | 21.6596 | 0 | 0.68734 | 27.7053 | 0.0060877 | 2.062 | 1.3853 | 0.018263 | 3.4655 |  | 7.4655 | 4 | 7.4655 | 21.6596 | 10.8298 | 20 | 20 | -9.1702 | -1062.9949
72 | 1.2 | 1.7833 | 9.7067 | 2 | 10.4 | 21.9864 | 0 | 0.69332 | 28.3987 | 0.0059811 | 2.0799 | 1.4199 | 0.017943 | 3.5178 |  | 7.5178 | 4 | 7.5178 | 21.9864 | 10.9932 | 20 | 20 | -9.0068 | -1072.0017
73 | 1.2167 | 1.7815 | 9.7008 | 2 | 10.4 | 22.3131 | 0 | 0.69919 | 29.0979 | 0.0058745 | 2.0976 | 1.4549 | 0.017623 | 3.5701 |  | 7.5701 | 4 | 7.5701 | 22.3131 | 11.1565 | 20 | 20 | -8.8435 | -1080.8452
74 | 1.2333 | 1.7797 | 9.695 | 2 | 10.4 | 22.6395 | 0 | 0.70496 | 29.8028 | 0.005768 | 2.1149 | 1.4901 | 0.017304 | 3.6223 |  | 7.6223 | 4 | 7.6223 | 22.6395 | 11.3198 | 20 | 20 | -8.6802 | -1089.5254
75 | 1.25 | 1.7779 | 9.6894 | 2 | 10.4 | 22.9657 | 0 | 0.71062 | 30.5134 | 0.0056615 | 2.1319 | 1.5257 | 0.016985 | 3.6745 |  | 7.6745 | 4 | 7.6745 | 22.9657 | 11.4829 | 20 | 20 | -8.5171 | -1098.0426
76 | 1.2667 | 1.7762 | 9.6838 | 2 | 10.4 | 23.2917 | 0 | 0.71618 | 31.2296 | 0.0055551 | 2.1485 | 1.5615 | 0.016665 | 3.7267 |  | 7.7267 | 4 | 7.7267 | 23.2917 | 11.6459 | 20 | 20 | -8.3541 | -1106.3967
77 | 1.2833 | 1.7745 | 9.6784 | 2 | 10.4 | 23.6174 | 0 | 0.72162 | 31.9512 | 0.0054488 | 2.1649 | 1.5976 | 0.016346 | 3.7788 |  | 7.7788 | 4 | 7.7788 | 23.6174 | 11.8087 | 20 | 20 | -8.1913 | -1114.588
78 | 1.3 | 1.7728 | 9.673 | 2 | 10.4 | 23.9427 | 0 | 0.72697 | 32.6782 | 0.0053426 | 2.1809 | 1.6339 | 0.016028 | 3.8308 |  | 7.8308 | 4 | 7.8308 | 23.9427 | 11.9714 | 20 | 20 | -8.0286 | -1122.6167
79 | 1.3167 | 1.7712 | 9.6678 | 2 | 10.4 | 24.2677 | 0 | 0.7322 | 33.4104 | 0.0052365 | 2.1966 | 1.6705 | 0.01571 | 3.8828 |  | 7.8828 | 4 | 7.8828 | 24.2677 | 12.1339 | 20 | 20 | -7.8661 | -1130.4828
80 | 1.3333 | 1.7696 | 9.6627 | 2 | 10.4 | 24.5924 | 0 | 0.73733 | 34.1477 | 0.0051305 | 2.212 | 1.7074 | 0.015392 | 3.9348 |  | 7.9348 | 4 | 7.9348 | 24.5924 | 12.2962 | 20 | 20 | -7.7038 | -1138.1866
81 | 1.35 | 1.768 | 9.6576 | 2 | 10.4 | 24.9166 | 0 | 0.74236 | 34.8901 | 0.0050247 | 2.2271 | 1.7445 | 0.015074 | 3.9867 |  | 7.9867 | 4 | 7.9867 | 24.9166 | 12.4583 | 20 | 20 | -7.5417 | -1145.7283
82 | 1.3667 | 1.7665 | 9.6527 | 2 | 10.4 | 25.2404 | 0 | 0.74728 | 35.6374 | 0.0049189 | 2.2418 | 1.7819 | 0.014757 | 4.0385 |  | 8.0385 | 4 | 8.0385 | 25.2404 | 12.6202 | 20 | 20 | -7.3798 | -1153.1081
83 | 1.3833 | 1.765 | 9.6479 | 2 | 10.4 | 25.5637 | 0 | 0.75209 | 36.3895 | 0.0048133 | 2.2563 | 1.8195 | 0.01444 | 4.0902 |  | 8.0902 | 4 | 8.0902 | 25.5637 | 12.7818 | 20 | 20 | -7.2182 | -1160.3263
84 | 1.4 | 1.7635 | 9.6432 | 2 | 10.4 | 25.8865 | 0 | 0.7568 | 37.1463 | 0.0047079 | 2.2704 | 1.8573 | 0.014124 | 4.1418 |  | 8.1418 | 4 | 8.1418 | 25.8865 | 12.9432 | 20 | 20 | -7.0568 | -1167.3831
85 | 1.4167 | 1.7621 | 9.6386 | 2 | 10.4 | 26.2087 | 0 | 0.7614 | 37.9077 | 0.0046026 | 2.2842 | 1.8954 | 0.013808 | 4.1934 |  | 8.1934 | 4 | 8.1934 | 26.2087 | 13.1044 | 20 | 20 | -6.8956 | -1174.2787
86 | 1.4333 | 1.7607 | 9.6341 | 2 | 10.4 | 26.5304 | 0 | 0.7659 | 38.6736 | 0.0044975 | 2.2977 | 1.9337 | 0.013493 | 4.2449 |  | 8.2449 | 4 | 8.2449 | 26.5304 | 13.2652 | 20 | 20 | -6.7348 | -1181.0135
87 | 1.45 | 1.7593 | 9.6297 | 2 | 10.4 | 26.8515 | 0 | 0.77029 | 39.4439 | 0.0043926 | 2.3109 | 1.9722 | 0.013178 | 4.2962 |  | 8.2962 | 4 | 8.2962 | 26.8515 | 13.4258 | 20 | 20 | -6.5742 | -1187.5877
88 | 1.4667 | 1.7579 | 9.6254 | 2 | 10.4 | 27.172 | 0 | 0.77458 | 40.2184 | 0.0042879 | 2.3237 | 2.0109 | 0.012864 | 4.3475 |  | 8.3475 | 4 | 8.3475 | 27.172 | 13.586 | 20 | 20 | -6.414 | -1194.0017
89 | 1.4833 | 1.7566 | 9.6212 | 2 | 10.4 | 27.4919 | 0 | 0.77876 | 40.9972 | 0.0041834 | 2.3363 | 2.0499 | 0.01255 | 4.3987 |  | 8.3987 | 4 | 8.3987 | 27.4919 | 13.7459 | 20 | 20 | -6.2541 | -1200.2558
90 | 1.5 | 1.7554 | 9.6172 | 2 | 10.4 | 27.811 | 0 | 0.78284 | 41.78 | 0.0040791 | 2.3485 | 2.089 | 0.012237 | 4.4498 |  | 8.4498 | 4 | 8.4498 | 27.811 | 13.9055 | 20 | 20 | -6.0945 | -1206.3503
91 | 1.5167 | 1.7541 | 9.6132 | 2 | 10.4 | 28.1295 | 0 | 0.78682 | 42.5669 | 0.003975 | 2.3605 | 2.1283 | 0.011925 | 4.5007 |  | 8.5007 | 4 | 8.5007 | 28.1295 | 14.0647 | 20 | 20 | -5.9353 | -1212.2855
92 | 1.5333 | 1.7529 | 9.6093 | 2 | 10.4 | 28.4472 | 0 | 0.79069 | 43.3575 | 0.0038711 | 2.3721 | 2.1679 | 0.011613 | 4.5516 |  | 8.5516 | 4 | 8.5516 | 28.4472 | 14.2236 | 20 | 20 | -5.7764 | -1218.0619
93 | 1.55 | 1.7517 | 9.6055 | 2 | 10.4 | 28.7642 | 0 | 0.79446 | 44.152 | 0.0037675 | 2.3834 | 2.2076 | 0.011303 | 4.6023 |  | 8.6023 | 4 | 8.6023 | 28.7642 | 14.3821 | 20 | 20 | -5.6179 | -1223.6798
94 | 1.5667 | 1.7506 | 9.6019 | 2 | 10.4 | 29.0804 | 0 | 0.79812 | 44.9501 | 0.0036642 | 2.3944 | 2.2475 | 0.010992 | 4.6529 |  | 8.6529 | 4 | 8.6529 | 29.0804 | 14.5402 | 20 | 20 | -5.4598 | -1229.1396
95 | 1.5833 | 1.7495 | 9.5983 | 2 | 10.4 | 29.3957 | 0 | 0.80168 | 45.7518 | 0.0035611 | 2.405 | 2.2876 | 0.010683 | 4.7033 |  | 8.7033 | 4 | 8.7033 | 29.3957 | 14.6979 | 20 | 20 | -5.3021 | -1234.4418
96 | 1.6 | 1.7484 | 9.5949 | 2 | 10.4 | 29.7102 | 0 | 0.80514 | 46.5569 | 0.0034582 | 2.4154 | 2.3278 | 0.010375 | 4.7536 |  | 8.7536 | 4 | 8.7536 | 29.7102 | 14.8551 | 20 | 20 | -5.1449 | -1239.5866
97 | 1.6167 | 1.7473 | 9.5915 | 2 | 10.4 | 30.0239 | 0 | 0.80849 | 47.3654 | 0.0033556 | 2.4255 | 2.3683 | 0.010067 | 4.8038 |  | 8.8038 | 4 | 8.8038 | 30.0239 | 15.0119 | 20 | 20 | -4.9881 | -1244.5747
98 | 1.6333 | 1.7463 | 9.5883 | 2 | 10.4 | 30.3366 | 0 | 0.81175 | 48.1772 | 0.0032534 | 2.4352 | 2.4089 | 0.0097601 | 4.8539 |  | 8.8539 | 4 | 8.8539 | 30.3366 | 15.1683 | 20 | 20 | -4.8317 | -1249.4064
99 | 1.65 | 1.7453 | 9.5851 | 2 | 10.4 | 30.6485 | 0 | 0.8149 | 48.9921 | 0.0031514 | 2.4447 | 2.4496 | 0.0094541 | 4.9038 |  | 8.9038 | 4 | 8.9038 | 30.6485 | 15.3242 | 20 | 20 | -4.6758 | -1254.0821
100 | 1.6667 | 1.7444 | 9.5821 | 2 | 10.4 | 30.9594 | 0 | 0.81795 | 49.81 | 0.0030497 | 2.4538 | 2.4905 | 0.009149 | 4.9535 |  | 8.9535 | 4 | 8.9535 | 30.9594 | 15.4797 | 20 | 20 | -4.5203 | -1258.6025
101 | 1.6833 | 1.7435 | 9.5791 | 2 | 10.4 | 31.2693 | 0 | 0.8209 | 50.6309 | 0.0029483 | 2.4627 | 2.5315 | 0.0088449 | 5.0031 |  | 9.0031 | 4 | 9.0031 | 31.2693 | 15.6346 | 20 | 20 | -4.3654 | -1262.9678
102 | 1.7 | 1.7426 | 9.5763 | 2 | 10.4 | 31.5782 | 0 | 0.82374 | 51.4547 | 0.0028472 | 2.4712 | 2.5727 | 0.0085417 | 5.0525 |  | 9.0525 | 4 | 9.0525 | 31.5782 | 15.7891 | 20 | 20 | -4.2109 | -1267.1787
103 | 1.7167 | 1.7417 | 9.5735 | 2 | 10.4 | 31.8861 | 0 | 0.82649 | 52.2812 | 0.0027465 | 2.4795 | 2.6141 | 0.0082394 | 5.1018 |  | 9.1018 | 4 | 9.1018 | 31.8861 | 15.943 | 20 | 20 | -4.057 | -1271.2357
104 | 1.7333 | 1.7409 | 9.5709 | 2 | 10.4 | 32.1929 | 0 | 0.82914 | 53.1103 | 0.0026461 | 2.4874 | 2.6555 | 0.0079382 | 5.1509 |  | 9.1509 | 4 | 9.1509 | 32.1929 | 16.0965 | 20 | 20 | -3.9035 | -1275.1392
105 | 1.75 | 1.7401 | 9.5683 | 2 | 10.4 | 32.4987 | 0 | 0.83168 | 53.942 | 0.002546 | 2.495 | 2.6971 | 0.007638 | 5.1998 |  | 9.1998 | 4 | 9.1998 | 32.4987 | 16.2493 | 20 | 20 | -3.7507 | -1278.8899
106 | 1.7667 | 1.7393 | 9.5659 | 2 | 10.4 | 32.8033 | 0 | 0.83413 | 54.7761 | 0.0024463 | 2.5024 | 2.7388 | 0.0073389 | 5.2485 |  | 9.2485 | 4 | 9.2485 | 32.8033 | 16.4017 | 20 | 20 | -3.5983 | -1282.4882
107 | 1.7833 | 1.7386 | 9.5635 | 2 | 10.4 | 33.1069 | 0 | 0.83648 | 55.6126 | 0.0023469 | 2.5094 | 2.7806 | 0.0070408 | 5.2971 |  | 9.2971 | 4 | 9.2971 | 33.1069 | 16.5534 | 20 | 20 | -3.4466 | -1285.9348
108 | 1.8 | 1.7379 | 9.5613 | 2 | 10.4 | 33.4093 | 0 | 0.83872 | 56.4513 | 0.002248 | 2.5162 | 2.8226 | 0.0067439 | 5.3455 |  | 9.3455 | 4 | 9.3455 | 33.4093 | 16.7046 | 20 | 20 | -3.2954 | -1289.2302
109 | 1.8167 | 1.7372 | 9.5591 | 2 | 10.4 | 33.7105 | 0 | 0.84087 | 57.2922 | 0.0021493 | 2.5226 | 2.8646 | 0.006448 | 5.3937 |  | 9.3937 | 4 | 9.3937 | 33.7105 | 16.8552 | 20 | 20 | -3.1448 | -1292.3749
110 | 1.8333 | 1.7366 | 9.5571 | 2 | 10.4 | 34.0105 | 0 | 0.84292 | 58.1351 | 0.0020511 | 2.5288 | 2.9068 | 0.0061533 | 5.4417 |  | 9.4417 | 4 | 9.4417 | 34.0105 | 17.0053 | 20 | 20 | -2.9947 | -1295.3697
111 | 1.85 | 1.736 | 9.5551 | 2 | 10.4 | 34.3093 | 0 | 0.84488 | 58.98 | 0.0019533 | 2.5346 | 2.949 | 0.0058598 | 5.4895 |  | 9.4895 | 4 | 9.4895 | 34.3093 | 17.1547 | 20 | 20 | -2.8453 | -1298.215
112 | 1.8667 | 1.7354 | 9.5533 | 2 | 10.4 | 34.6069 | 0 | 0.84673 | 59.8267 | 0.0018558 | 2.5402 | 2.9913 | 0.0055674 | 5.5371 |  | 9.5371 | 4 | 9.5371 | 34.6069 | 17.3035 | 20 | 20 | -2.6965 | -1300.9115
113 | 1.8833 | 1.7348 | 9.5515 | 2 | 10.4 | 34.9032 | 0 | 0.84849 | 60.6752 | 0.0017588 | 2.5455 | 3.0338 | 0.0052763 | 5.5845 |  | 9.5845 | 4 | 9.5845 | 34.9032 | 17.4516 | 20 | 20 | -2.5484 | -1303.4599
114 | 1.9 | 1.7343 | 9.5498 | 2 | 10.4 | 35.1982 | 0 | 0.85015 | 61.5254 | 0.0016621 | 2.5505 | 3.0763 | 0.0049864 | 5.6317 |  | 9.6317 | 4 | 9.6317 | 35.1982 | 17.5991 | 20 | 20 | -2.4009 | -1305.8608
115 | 1.9167 | 1.7338 | 9.5483 | 2 | 10.4 | 35.492 | 0 | 0.85172 | 62.3771 | 0.0015659 | 2.5552 | 3.1189 | 0.0046978 | 5.6787 |  | 9.6787 | 4 | 9.6787 | 35.492 | 17.746 | 20 | 20 | -2.254 | -1308.1148
116 | 1.9333 | 1.7334 | 9.5468 | 2 | 10.4 | 35.7844 | 0 | 0.85319 | 63.2303 | 0.0014701 | 2.5596 | 3.1615 | 0.0044104 | 5.7255 |  | 9.7255 | 4 | 9.7255 | 35.7844 | 17.8922 | 20 | 20 | -2.1078 | -1310.2227
117 | 1.95 | 1.7329 | 9.5454 | 2 | 10.4 | 36.0754 | 0 | 0.85457 | 64.0848 | 0.0013748 | 2.5637 | 3.2042 | 0.0041243 | 5.7721 |  | 9.7721 | 4 | 9.7721 | 36.0754 | 18.0377 | 20 | 20 | -1.9623 | -1312.185
118 | 1.9667 | 1.7325 | 9.5442 | 2 | 10.4 | 36.3651 | 0 | 0.85585 | 64.9407 | 0.0012799 | 2.5675 | 3.247 | 0.0038396 | 5.8184 |  | 9.8184 | 4 | 9.8184 | 36.3651 | 18.1825 | 20 | 20 | -1.8175 | -1314.0024
119 | 1.9833 | 1.7322 | 9.543 | 2 | 10.4 | 36.6533 | 0 | 0.85703 | 65.7977 | 0.0011854 | 2.5711 | 3.2899 | 0.0035562 | 5.8645 |  | 9.8645 | 4 | 9.8645 | 36.6533 | 18.3267 | 20 | 20 | -1.6733 | -1315.6758
120 | 2 | 1.7318 | 9.5419 | 2 | 10.4 | 36.9402 | 0 | 0.85812 | 66.6558 | 0.0010914 | 2.5744 | 3.3328 | 0.0032742 | 5.9104 |  | 9.9104 | 4 | 9.9104 | 36.9402 | 18.4701 | 20 | 20 | -1.5299 | -1317.2056
121 | 2.0167 | 1.7315 | 9.5409 | 2 | 10.4 | 37.2256 | 0 | 0.85912 | 67.515 | 0.00099784 | 2.5774 | 3.3757 | 0.0029935 | 5.9561 |  | 9.9561 | 4 | 9.9561 | 37.2256 | 18.6128 | 20 | 20 | -1.3872 | -1318.5928
122 | 2.0333 | 1.7312 | 9.54 | 2 | 10.4 | 37.5096 | 0 | 0.86002 | 68.375 | 0.00090476 | 2.5801 | 3.4187 | 0.0027143 | 6.0015 |  | 10.0015 | 4 | 10.0015 | 37.5096 | 18.7548 | 20 | 20 | -1.2452 | -1319.838
123 | 2.05 | 1.731 | 9.5392 | 2 | 10.4 | 37.7921 | 0 | 0.86084 | 69.2358 | 0.00081215 | 2.5825 | 3.4618 | 0.0024365 | 6.0467 |  | 10.0467 | 4 | 10.0467 | 37.7921 | 18.8961 | 20 | 20 | -1.1039 | -1320.942
124 | 2.0667 | 1.7308 | 9.5384 | 2 | 10.4 | 38.0731 | 0 | 0.86156 | 70.0974 | 0.00072002 | 2.5847 | 3.5049 | 0.0021601 | 6.0917 |  | 10.0917 | 4 | 10.0917 | 38.0731 | 19.0366 | 20 | 20 | -0.96344 | -1321.9054
125 | 2.0833 | 1.7306 | 9.5378 | 2 | 10.4 | 38.3526 | 0 | 0.86219 | 70.9596 | 0.00062838 | 2.5866 | 3.548 | 0.0018851 | 6.1364 |  | 10.1364 | 4 | 10.1364 | 38.3526 | 19.1763 | 20 | 20 | -0.82369 | -1322.7291
126 | 2.1 | 1.7304 | 9.5373 | 2 | 10.4 | 38.6306 | 0 | 0.86272 | 71.8223 | 0.00053723 | 2.5882 | 3.5911 | 0.0016117 | 6.1809 |  | 10.1809 | 4 | 10.1809 | 38.6306 | 19.3153 | 20 | 20 | -0.68471 | -1323.4138
127 | 2.1167 | 1.7303 | 9.5368 | 2 | 10.4 | 38.907 | 0 | 0.86317 | 72.6855 | 0.00044658 | 2.5895 | 3.6343 | 0.0013398 | 6.2251 |  | 10.2251 | 4 | 10.2251 | 38.907 | 19.4535 | 20 | 20 | -0.5465 | -1323.9603
128 | 2.1333 | 1.7301 | 9.5365 | 2 | 10.4 | 39.1818 | 0 | 0.86353 | 73.549 | 0.00035644 | 2.5906 | 3.6774 | 0.0010693 | 6.2691 |  | 10.2691 | 4 | 10.2691 | 39.1818 | 19.5909 | 20 | 20 | -0.40908 | -1324.3694
129 | 2.15 | 1.7301 | 9.5362 | 2 | 10.4 | 39.4551 | 0 | 0.86379 | 74.4128 | 0.00026681 | 2.5914 | 3.7206 | 0.00080043 | 6.3128 |  | 10.3128 | 4 | 10.3128 | 39.4551 | 19.7276 | 20 | 20 | -0.27245 | -1324.6418
130 | 2.1667 | 1.73 | 9.536 | 2 | 10.4 | 39.7268 | 0 | 0.86397 | 75.2768 | 0.0001777 | 2.5919 | 3.7638 | 0.00053309 | 6.3563 |  | 10.3563 | 4 | 10.3563 | 39.7268 | 19.8634 | 20 | 20 | -0.13662 | -1324.7784
131 | 2.1833 | 1.73 | 9.5359 | 2 | 10.4 | 39.9968 | 0 | 0.86406 | 76.1408 | 8.9108e-05 | 2.5922 | 3.807 | 0.00026732 | 6.3995 |  | 10.3995 | 4 | 10.3995 | 39.9968 | 19.9984 | 20 | 20 | -0.0016069 | -1324.78
132 | 2.2 | 1.73 | 9.5359 | 2 | 10.4 | 40.2652 | 0 | 0.86406 | 77.0049 | 1.0481e-06 | 2.5922 | 3.8502 | 3.1443e-06 | 6.4424 |  | 10.4424 | 4 | 10.4424 | 40.2652 | 20.1326 | 20 | 20 | 0.13259 | -1324.6475
133 | 2.2167 | 1.73 | 9.536 | 2 | 10.4 | 40.5319 | 0 | 0.86397 | 77.8688 | -8.6477e-05 | 2.5919 | 3.8934 | -0.00025943 | 6.4851 |  | 10.4851 | 4 | 10.4851 | 40.5319 | 20.266 | 20 | 20 | 0.26595 | -1324.3815
134 | 2.2333 | 1.7301 | 9.5362 | 2 | 10.4 | 40.797 | 0 | 0.8638 | 78.7326 | -0.00017346 | 2.5914 | 3.9366 | -0.00052038 | 6.5275 |  | 10.5275 | 4 | 10.5275 | 40.797 | 20.3985 | 20 | 20 | 0.39848 | -1323.983
135 | 2.25 | 1.7301 | 9.5365 | 2 | 10.4 | 41.0603 | 0 | 0.86354 | 79.5962 | -0.0002599 | 2.5906 | 3.9798 | -0.0007797 | 6.5697 |  | 10.5697 | 4 | 10.5697 | 41.0603 | 20.5302 | 20 | 20 | 0.53016 | -1323.4529
136 | 2.2667 | 1.7303 | 9.5368 | 2 | 10.4 | 41.322 | 0 | 0.86319 | 80.4594 | -0.00034579 | 2.5896 | 4.023 | -0.0010374 | 6.6115 |  | 10.6115 | 4 | 10.6115 | 41.322 | 20.661 | 20 | 20 | 0.66099 | -1322.7919
137 | 2.2833 | 1.7304 | 9.5372 | 2 | 10.4 | 41.5819 | 0 | 0.86276 | 81.3221 | -0.00043112 | 2.5883 | 4.0661 | -0.0012933 | 6.6531 |  | 10.6531 | 4 | 10.6531 | 41.5819 | 20.791 | 20 | 20 | 0.79095 | -1322.0009
138 | 2.3 | 1.7305 | 9.5378 | 2 | 10.4 | 41.8401 | 0 | 0.86225 | 82.1844 | -0.00051588 | 2.5867 | 4.1092 | -0.0015476 | 6.6944 |  | 10.6944 | 4 | 10.6944 | 41.8401 | 20.92 | 20 | 20 | 0.92005 | -1321.0809
139 | 2.3167 | 1.7307 | 9.5384 | 2 | 10.4 | 42.0965 | 0 | 0.86165 | 83.046 | -0.00060008 | 2.5849 | 4.1523 | -0.0018002 | 6.7354 |  | 10.7354 | 4 | 10.7354 | 42.0965 | 21.0483 | 20 | 20 | 1.0483 | -1320.0326
140 | 2.3333 | 1.7309 | 9.539 | 2 | 10.4 | 42.3512 | 0 | 0.86096 | 83.907 | -0.00068371 | 2.5829 | 4.1954 | -0.0020511 | 6.7762 |  | 10.7762 | 4 | 10.7762 | 42.3512 | 21.1756 | 20 | 20 | 1.1756 | -1318.857
141 | 2.35 | 1.7312 | 9.5398 | 2 | 10.4 | 42.6041 | 0 | 0.8602 | 84.7672 | -0.00076676 | 2.5806 | 4.2384 | -0.0023003 | 6.8167 |  | 10.8167 | 4 | 10.8167 | 42.6041 | 21.302 | 20 | 20 | 1.302 | -1317.555
142 | 2.3667 | 1.7315 | 9.5407 | 2 | 10.4 | 42.8551 | 0 | 0.85935 | 85.6265 | -0.00084923 | 2.578 | 4.2813 | -0.0025477 | 6.8568 |  | 10.8568 | 4 | 10.8568 | 42.8551 | 21.4276 | 20 | 20 | 1.4276 | -1316.1274
143 | 2.3833 | 1.7317 | 9.5416 | 2 | 10.4 | 43.1044 | 0 | 0.85842 | 86.485 | -0.00093111 | 2.5753 | 4.3242 | -0.0027933 | 6.8967 |  | 10.8967 | 4 | 10.8967 | 43.1044 | 21.5522 | 20 | 20 | 1.5522 | -1314.5752
144 | 2.4 | 1.7321 | 9.5426 | 2 | 10.4 | 43.3518 | 0 | 0.8574 | 87.3424 | -0.0010124 | 2.5722 | 4.3671 | -0.0030372 | 6.9363 |  | 10.9363 | 4 | 10.9363 | 43.3518 | 21.6759 | 20 | 20 | 1.6759 | -1312.8993
145 | 2.4167 | 1.7324 | 9.5437 | 2 | 10.4 | 43.5974 | 0 | 0.85631 | 88.1987 | -0.0010931 | 2.5689 | 4.4099 | -0.0032793 | 6.9756 |  | 10.9756 | 4 | 10.9756 | 43.5974 | 21.7987 | 20 | 20 | 1.7987 | -1311.1006
146 | 2.4333 | 1.7328 | 9.5449 | 2 | 10.4 | 43.8412 | 0 | 0.85514 | 89.0538 | -0.0011732 | 2.5654 | 4.4527 | -0.0035195 | 7.0146 |  | 11.0146 | 4 | 11.0146 | 43.8412 | 21.9206 | 20 | 20 | 1.9206 | -1309.18
147 | 2.45 | 1.7332 | 9.5461 | 2 | 10.4 | 44.083 | 0 | 0.85389 | 89.9077 | -0.0012527 | 2.5617 | 4.4954 | -0.003758 | 7.0533 |  | 11.0533 | 4 | 11.0533 | 44.083 | 22.0415 | 20 | 20 | 2.0415 | -1307.1385
148 | 2.4667 | 1.7336 | 9.5474 | 2 | 10.4 | 44.323 | 0 | 0.85255 | 90.7603 | -0.0013315 | 2.5577 | 4.538 | -0.0039946 | 7.0917 |  | 11.0917 | 4 | 11.0917 | 44.323 | 22.1615 | 20 | 20 | 2.1615 | -1304.977
149 | 2.4833 | 1.734 | 9.5489 | 2 | 10.4 | 44.5611 | 0 | 0.85114 | 91.6114 | -0.0014098 | 2.5534 | 4.5806 | -0.0042294 | 7.1298 |  | 11.1298 | 4 | 11.1298 | 44.5611 | 22.2805 | 20 | 20 | 2.2805 | -1302.6964
150 | 2.5 | 1.7345 | 9.5503 | 2 | 10.4 | 44.7973 | 0 | 0.84966 | 92.4611 | -0.0014874 | 2.549 | 4.6231 | -0.0044623 | 7.1676 |  | 11.1676 | 4 | 11.1676 | 44.7973 | 22.3986 | 20 | 20 | 2.3986 | -1300.2978
151 | 2.5167 | 1.735 | 9.5519 | 2 | 10.4 | 45.0315 | 0 | 0.84809 | 93.3092 | -0.0015645 | 2.5443 | 4.6655 | -0.0046934 | 7.205 |  | 11.205 | 4 | 11.205 | 45.0315 | 22.5158 | 20 | 20 | 2.5158 | -1297.782
152 | 2.5333 | 1.7355 | 9.5535 | 2 | 10.4 | 45.2638 | 0 | 0.84645 | 94.1556 | -0.0016408 | 2.5394 | 4.7078 | -0.0049225 | 7.2422 |  | 11.2422 | 4 | 11.2422 | 45.2638 | 22.6319 | 20 | 20 | 2.6319 | -1295.1501
153 | 2.55 | 1.736 | 9.5553 | 2 | 10.4 | 45.4942 | 0 | 0.84473 | 95.0003 | -0.0017166 | 2.5342 | 4.75 | -0.0051498 | 7.2791 |  | 11.2791 | 4 | 11.2791 | 45.4942 | 22.7471 | 20 | 20 | 2.7471 | -1292.403
154 | 2.5667 | 1.7366 | 9.5571 | 2 | 10.4 | 45.7226 | 0 | 0.84294 | 95.8433 | -0.0017917 | 2.5288 | 4.7922 | -0.0053752 | 7.3156 |  | 11.3156 | 4 | 11.3156 | 45.7226 | 22.8613 | 20 | 20 | 2.8613 | -1289.5417
155 | 2.5833 | 1.7372 | 9.5589 | 2 | 10.4 | 45.9491 | 0 | 0.84108 | 96.6844 | -0.0018662 | 2.5232 | 4.8342 | -0.0055987 | 7.3518 |  | 11.3518 | 4 | 11.3518 | 45.9491 | 22.9745 | 20 | 20 | 2.9745 | -1286.5672
156 | 2.6 | 1.7378 | 9.5609 | 2 | 10.4 | 46.1735 | 0 | 0.83914 | 97.5235 | -0.0019401 | 2.5174 | 4.8762 | -0.0058202 | 7.3878 |  | 11.3878 | 4 | 11.3878 | 46.1735 | 23.0868 | 20 | 20 | 3.0868 | -1283.4804
157 | 2.6167 | 1.7384 | 9.5629 | 2 | 10.4 | 46.396 | 0 | 0.83712 | 98.3606 | -0.0020133 | 2.5114 | 4.918 | -0.0060398 | 7.4234 |  | 11.4234 | 4 | 11.4234 | 46.396 | 23.198 | 20 | 20 | 3.198 | -1280.2824
158 | 2.6333 | 1.7391 | 9.565 | 2 | 10.4 | 46.6165 | 0 | 0.83504 | 99.1957 | -0.0020858 | 2.5051 | 4.9598 | -0.0062575 | 7.4586 |  | 11.4586 | 4 | 11.4586 | 46.6165 | 23.3082 | 20 | 20 | 3.3082 | -1276.9742
159 | 2.65 | 1.7397 | 9.5671 | 2 | 10.4 | 46.835 | 0 | 0.83288 | 100.0285 | -0.0021577 | 2.4986 | 5.0014 | -0.0064732 | 7.4936 |  | 11.4936 | 4 | 11.4936 | 46.835 | 23.4175 | 20 | 20 | 3.4175 | -1273.5567
160 | 2.6667 | 1.7404 | 9.5693 | 2 | 10.4 | 47.0514 | 0 | 0.83065 | 100.8592 | -0.002229 | 2.492 | 5.043 | -0.0066869 | 7.5282 |  | 11.5282 | 4 | 11.5282 | 47.0514 | 23.5257 | 20 | 20 | 3.5257 | -1270.031
161 | 2.6833 | 1.7411 | 9.5716 | 2 | 10.4 | 47.2658 | 0 | 0.82835 | 101.6875 | -0.0022996 | 2.4851 | 5.0844 | -0.0068987 | 7.5625 |  | 11.5625 | 4 | 11.5625 | 47.2658 | 23.6329 | 20 | 20 | 3.6329 | -1266.3981
162 | 2.7 | 1.7419 | 9.574 | 2 | 10.4 | 47.4782 | 0 | 0.82598 | 102.5135 | -0.0023695 | 2.4779 | 5.1257 | -0.0071085 | 7.5965 |  | 11.5965 | 4 | 11.5965 | 47.4782 | 23.7391 | 20 | 20 | 3.7391 | -1262.659
163 | 2.7167 | 1.7426 | 9.5765 | 2 | 10.4 | 47.6885 | 0 | 0.82354 | 103.3371 | -0.0024388 | 2.4706 | 5.1669 | -0.0073163 | 7.6302 |  | 11.6302 | 4 | 11.6302 | 47.6885 | 23.8443 | 20 | 20 | 3.8443 | -1258.8147
164 | 2.7333 | 1.7434 | 9.579 | 2 | 10.4 | 47.8968 | 0 | 0.82104 | 104.1581 | -0.0025073 | 2.4631 | 5.2079 | -0.007522 | 7.6635 |  | 11.6635 | 4 | 11.6635 | 47.8968 | 23.9484 | 20 | 20 | 3.9484 | -1254.8663
165 | 2.75 | 1.7442 | 9.5815 | 2 | 10.4 | 48.103 | 0 | 0.81846 | 104.9766 | -0.0025753 | 2.4554 | 5.2488 | -0.0077258 | 7.6965 |  | 11.6965 | 4 | 11.6965 | 48.103 | 24.0515 | 20 | 20 | 4.0515 | -1250.8148
166 | 2.7667 | 1.7451 | 9.5842 | 2 | 10.4 | 48.3072 | 0 | 0.81582 | 105.7924 | -0.0026425 | 2.4475 | 5.2896 | -0.0079275 | 7.7291 |  | 11.7291 | 4 | 11.7291 | 48.3072 | 24.1536 | 20 | 20 | 4.1536 | -1246.6612
167 | 2.7833 | 1.7459 | 9.5869 | 2 | 10.4 | 48.5092 | 0 | 0.81311 | 106.6055 | -0.0027091 | 2.4393 | 5.3303 | -0.0081273 | 7.7615 |  | 11.7615 | 4 | 11.7615 | 48.5092 | 24.2546 | 20 | 20 | 4.2546 | -1242.4066
168 | 2.8 | 1.7468 | 9.5897 | 2 | 10.4 | 48.7092 | 0 | 0.81033 | 107.4158 | -0.002775 | 2.431 | 5.3708 | -0.0083249 | 7.7935 |  | 11.7935 | 4 | 11.7935 | 48.7092 | 24.3546 | 20 | 20 | 4.3546 | -1238.052
169 | 2.8167 | 1.7477 | 9.5925 | 2 | 10.4 | 48.907 | 0 | 0.80749 | 108.2233 | -0.0028402 | 2.4225 | 5.4112 | -0.0085206 | 7.8251 |  | 11.8251 | 4 | 11.8251 | 48.907 | 24.4535 | 20 | 20 | 4.4535 | -1233.5985
170 | 2.8333 | 1.7486 | 9.5954 | 2 | 10.4 | 49.1028 | 0 | 0.80459 | 109.0279 | -0.0029047 | 2.4138 | 5.4514 | -0.0087141 | 7.8564 |  | 11.8564 | 4 | 11.8564 | 49.1028 | 24.5514 | 20 | 20 | 4.5514 | -1229.0471
171 | 2.85 | 1.7495 | 9.5984 | 2 | 10.4 | 49.2965 | 0 | 0.80162 | 109.8295 | -0.0029686 | 2.4049 | 5.4915 | -0.0089057 | 7.8874 |  | 11.8874 | 4 | 11.8874 | 49.2965 | 24.6482 | 20 | 20 | 4.6482 | -1224.3989
172 | 2.8667 | 1.7504 | 9.6014 | 2 | 10.4 | 49.488 | 0 | 0.79859 | 110.6281 | -0.0030317 | 2.3958 | 5.5314 | -0.0090951 | 7.9181 |  | 11.9181 | 4 | 11.9181 | 49.488 | 24.744 | 20 | 20 | 4.744 | -1219.6549
173 | 2.8833 | 1.7514 | 9.6045 | 2 | 10.4 | 49.6774 | 0 | 0.79549 | 111.4236 | -0.0030942 | 2.3865 | 5.5712 | -0.0092825 | 7.9484 |  | 11.9484 | 4 | 11.9484 | 49.6774 | 24.8387 | 20 | 20 | 4.8387 | -1214.8162
174 | 2.9 | 1.7524 | 9.6077 | 2 | 10.4 | 49.8647 | 0 | 0.79234 | 112.2159 | -0.0031559 | 2.377 | 5.6108 | -0.0094678 | 7.9783 |  | 11.9783 | 4 | 11.9783 | 49.8647 | 24.9323 | 20 | 20 | 4.9323 | -1209.8838
175 | 2.9167 | 1.7534 | 9.6109 | 2 | 10.4 | 50.0498 | 0 | 0.78912 | 113.0051 | -0.003217 | 2.3674 | 5.6503 | -0.009651 | 8.008 |  | 12.008 | 4 | 12.008 | 50.0498 | 25.0249 | 20 | 20 | 5.0249 | -1204.859
176 | 2.9333 | 1.7544 | 9.6142 | 2 | 10.4 | 50.2328 | 0 | 0.78584 | 113.7909 | -0.0032774 | 2.3575 | 5.6895 | -0.0098322 | 8.0372 |  | 12.0372 | 4 | 12.0372 | 50.2328 | 25.1164 | 20 | 20 | 5.1164 | -1199.7426
177 | 2.95 | 1.7555 | 9.6175 | 2 | 10.4 | 50.4136 | 0 | 0.78251 | 114.5734 | -0.0033371 | 2.3475 | 5.7287 | -0.010011 | 8.0662 |  | 12.0662 | 4 | 12.0662 | 50.4136 | 25.2068 | 20 | 20 | 5.2068 | -1194.5357
178 | 2.9667 | 1.7565 | 9.6209 | 2 | 10.4 | 50.5923 | 0 | 0.77911 | 115.3525 | -0.003396 | 2.3373 | 5.7676 | -0.010188 | 8.0948 |  | 12.0948 | 4 | 12.0948 | 50.5923 | 25.2962 | 20 | 20 | 5.2962 | -1189.2396
179 | 2.9833 | 1.7576 | 9.6243 | 2 | 10.4 | 50.7689 | 0 | 0.77566 | 116.1282 | -0.0034543 | 2.327 | 5.8064 | -0.010363 | 8.123 |  | 12.123 | 4 | 12.123 | 50.7689 | 25.3844 | 20 | 20 | 5.3844 | -1183.8551
180 | 3 | 1.7587 | 9.6279 | 2 | 10.4 | 50.9432 | 0 | 0.77215 | 116.9003 | -0.0035119 | 2.3164 | 5.845 | -0.010536 | 8.1509 |  | 12.1509 | 4 | 12.1509 | 50.9432 | 25.4716 | 20 | 20 | 5.4716 | -1178.3835
181 | 3.0167 | 1.7598 | 9.6314 | 2 | 10.4 | 51.1154 | 0 | 0.76858 | 117.6689 | -0.0035687 | 2.3057 | 5.8834 | -0.010706 | 8.1785 |  | 12.1785 | 4 | 12.1785 | 51.1154 | 25.5577 | 20 | 20 | 5.5577 | -1172.8258
182 | 3.0333 | 1.761 | 9.635 | 2 | 10.4 | 51.2855 | 0 | 0.76495 | 118.4339 | -0.0036249 | 2.2949 | 5.9217 | -0.010875 | 8.2057 |  | 12.2057 | 4 | 12.2057 | 51.2855 | 25.6427 | 20 | 20 | 5.6427 | -1167.1831
183 | 3.05 | 1.7621 | 9.6387 | 2 | 10.4 | 51.4533 | 0 | 0.76127 | 119.1951 | -0.0036804 | 2.2838 | 5.9598 | -0.011041 | 8.2325 |  | 12.2325 | 4 | 12.2325 | 51.4533 | 25.7267 | 20 | 20 | 5.7267 | -1161.4564
184 | 3.0667 | 1.7633 | 9.6425 | 2 | 10.4 | 51.619 | 0 | 0.75754 | 119.9527 | -0.0037351 | 2.2726 | 5.9976 | -0.011205 | 8.259 |  | 12.259 | 4 | 12.259 | 51.619 | 25.8095 | 20 | 20 | 5.8095 | -1155.647
185 | 3.0833 | 1.7645 | 9.6463 | 2 | 10.4 | 51.7825 | 0 | 0.75375 | 120.7064 | -0.0037891 | 2.2612 | 6.0353 | -0.011367 | 8.2852 |  | 12.2852 | 4 | 12.2852 | 51.7825 | 25.8912 | 20 | 20 | 5.8912 | -1149.7557
186 | 3.1 | 1.7657 | 9.6501 | 2 | 10.4 | 51.9438 | 0 | 0.7499 | 121.4563 | -0.0038424 | 2.2497 | 6.0728 | -0.011527 | 8.311 |  | 12.311 | 4 | 12.311 | 51.9438 | 25.9719 | 20 | 20 | 5.9719 | -1143.7838
187 | 3.1167 | 1.7669 | 9.654 | 2 | 10.4 | 52.1029 | 0 | 0.74601 | 122.2023 | -0.003895 | 2.238 | 6.1101 | -0.011685 | 8.3365 |  | 12.3365 | 4 | 12.3365 | 52.1029 | 26.0514 | 20 | 20 | 6.0514 | -1137.7324
188 | 3.1333 | 1.7681 | 9.6579 | 2 | 10.4 | 52.2598 | 0 | 0.74206 | 122.9444 | -0.0039469 | 2.2262 | 6.1472 | -0.011841 | 8.3616 |  | 12.3616 | 4 | 12.3616 | 52.2598 | 26.1299 | 20 | 20 | 6.1299 | -1131.6025
189 | 3.15 | 1.7694 | 9.6619 | 2 | 10.4 | 52.4145 | 0 | 0.73806 | 123.6825 | -0.0039981 | 2.2142 | 6.1841 | -0.011994 | 8.3863 |  | 12.3863 | 4 | 12.3863 | 52.4145 | 26.2073 | 20 | 20 | 6.2073 | -1125.3953
190 | 3.1667 | 1.7706 | 9.666 | 2 | 10.4 | 52.567 | 0 | 0.73402 | 124.4165 | -0.0040486 | 2.202 | 6.2208 | -0.012146 | 8.4107 |  | 12.4107 | 4 | 12.4107 | 52.567 | 26.2835 | 20 | 20 | 6.2835 | -1119.1117
191 | 3.1833 | 1.7719 | 9.6701 | 2 | 10.4 | 52.7174 | 0 | 0.72992 | 125.1464 | -0.0040983 | 2.1898 | 6.2573 | -0.012295 | 8.4348 |  | 12.4348 | 4 | 12.4348 | 52.7174 | 26.3587 | 20 | 20 | 6.3587 | -1112.7531
192 | 3.2 | 1.7732 | 9.6742 | 2 | 10.4 | 52.8655 | 0 | 0.72577 | 125.8722 | -0.0041473 | 2.1773 | 6.2936 | -0.012442 | 8.4585 |  | 12.4585 | 4 | 12.4585 | 52.8655 | 26.4327 | 20 | 20 | 6.4327 | -1106.3203
193 | 3.2167 | 1.7745 | 9.6784 | 2 | 10.4 | 53.0114 | 0 | 0.72157 | 126.5937 | -0.0041956 | 2.1647 | 6.3297 | -0.012587 | 8.4818 |  | 12.4818 | 4 | 12.4818 | 53.0114 | 26.5057 | 20 | 20 | 6.5057 | -1099.8146
194 | 3.2333 | 1.7758 | 9.6827 | 2 | 10.4 | 53.1551 | 0 | 0.71733 | 127.3111 | -0.0042432 | 2.152 | 6.3656 | -0.01273 | 8.5048 |  | 12.5048 | 4 | 12.5048 | 53.1551 | 26.5776 | 20 | 20 | 6.5776 | -1093.2371
195 | 3.25 | 1.7772 | 9.687 | 2 | 10.4 | 53.2966 | 0 | 0.71304 | 128.0241 | -0.0042901 | 2.1391 | 6.4012 | -0.01287 | 8.5275 |  | 12.5275 | 4 | 12.5275 | 53.2966 | 26.6483 | 20 | 20 | 6.6483 | -1086.5888
196 | 3.2667 | 1.7785 | 9.6913 | 2 | 10.4 | 53.4359 | 0 | 0.70871 | 128.7328 | -0.0043362 | 2.1261 | 6.4366 | -0.013009 | 8.5497 |  | 12.5497 | 4 | 12.5497 | 53.4359 | 26.718 | 20 | 20 | 6.718 | -1079.8708
197 | 3.2833 | 1.7799 | 9.6957 | 2 | 10.4 | 53.573 | 0 | 0.70432 | 129.4371 | -0.0043816 | 2.113 | 6.4719 | -0.013145 | 8.5717 |  | 12.5717 | 4 | 12.5717 | 53.573 | 26.7865 | 20 | 20 | 6.7865 | -1073.0843
198 | 3.3 | 1.7813 | 9.7001 | 2 | 10.4 | 53.7079 | 0 | 0.6999 | 130.137 | -0.0044264 | 2.0997 | 6.5069 | -0.013279 | 8.5933 |  | 12.5933 | 4 | 12.5933 | 53.7079 | 26.8539 | 20 | 20 | 6.8539 | -1066.2304
199 | 3.3167 | 1.7827 | 9.7046 | 2 | 10.4 | 53.8406 | 0 | 0.69543 | 130.8325 | -0.0044703 | 2.0863 | 6.5416 | -0.013411 | 8.6145 |  | 12.6145 | 4 | 12.6145 | 53.8406 | 26.9203 | 20 | 20 | 6.9203 | -1059.3101
200 | 3.3333 | 1.7841 | 9.7091 | 2 | 10.4 | 53.971 | 0 | 0.69091 | 131.5234 | -0.0045136 | 2.0727 | 6.5762 | -0.013541 | 8.6354 |  | 12.6354 | 4 | 12.6354 | 53.971 | 26.9855 | 20 | 20 | 6.9855 | -1052.3245
201 | 3.35 | 1.7855 | 9.7136 | 2 | 10.4 | 54.0993 | 0 | 0.68636 | 132.2097 | -0.0045562 | 2.0591 | 6.6105 | -0.013668 | 8.6559 |  | 12.6559 | 4 | 12.6559 | 54.0993 | 27.0497 | 20 | 20 | 7.0497 | -1045.2749
202 | 3.3667 | 1.787 | 9.7182 | 2 | 10.4 | 54.2254 | 0 | 0.68176 | 132.8915 | -0.004598 | 2.0453 | 6.6446 | -0.013794 | 8.6761 |  | 12.6761 | 4 | 12.6761 | 54.2254 | 27.1127 | 20 | 20 | 7.1127 | -1038.1622
203 | 3.3833 | 1.7884 | 9.7229 | 2 | 10.4 | 54.3492 | 0 | 0.67712 | 133.5686 | -0.0046391 | 2.0314 | 6.6784 | -0.013917 | 8.6959 |  | 12.6959 | 4 | 12.6959 | 54.3492 | 27.1746 | 20 | 20 | 7.1746 | -1030.9876
204 | 3.4 | 1.7899 | 9.7276 | 2 | 10.4 | 54.4708 | 0 | 0.67244 | 134.241 | -0.0046795 | 2.0173 | 6.7121 | -0.014038 | 8.7153 |  | 12.7153 | 4 | 12.7153 | 54.4708 | 27.2354 | 20 | 20 | 7.2354 | -1023.7522
205 | 3.4167 | 1.7913 | 9.7323 | 2 | 10.4 | 54.5903 | 0 | 0.66772 | 134.9088 | -0.0047192 | 2.0032 | 6.7454 | -0.014157 | 8.7344 |  | 12.7344 | 4 | 12.7344 | 54.5903 | 27.2951 | 20 | 20 | 7.2951 | -1016.4571
206 | 3.4333 | 1.7928 | 9.737 | 2 | 10.4 | 54.7075 | 0 | 0.66296 | 135.5717 | -0.0047581 | 1.9889 | 6.7786 | -0.014274 | 8.7532 |  | 12.7532 | 4 | 12.7532 | 54.7075 | 27.3538 | 20 | 20 | 7.3538 | -1009.1033
207 | 3.45 | 1.7943 | 9.7418 | 2 | 10.4 | 54.8225 | 0 | 0.65817 | 136.2299 | -0.0047963 | 1.9745 | 6.8115 | -0.014389 | 8.7716 |  | 12.7716 | 4 | 12.7716 | 54.8225 | 27.4113 | 20 | 20 | 7.4113 | -1001.692
208 | 3.4667 | 1.7958 | 9.7467 | 2 | 10.4 | 54.9354 | 0 | 0.65333 | 136.8832 | -0.0048338 | 1.96 | 6.8442 | -0.014502 | 8.7897 |  | 12.7897 | 4 | 12.7897 | 54.9354 | 27.4677 | 20 | 20 | 7.4677 | -994.2243
209 | 3.4833 | 1.7974 | 9.7515 | 2 | 10.4 | 55.046 | 0 | 0.64846 | 137.5317 | -0.0048706 | 1.9454 | 6.8766 | -0.014612 | 8.8074 |  | 12.8074 | 4 | 12.8074 | 55.046 | 27.523 | 20 | 20 | 7.523 | -986.7013
210 | 3.5 | 1.7989 | 9.7564 | 2 | 10.4 | 55.1544 | 0 | 0.64356 | 138.1752 | -0.0049067 | 1.9307 | 6.9088 | -0.01472 | 8.8247 |  | 12.8247 | 4 | 12.8247 | 55.1544 | 27.5772 | 20 | 20 | 7.5772 | -979.1241
211 | 3.5167 | 1.8004 | 9.7614 | 2 | 10.4 | 55.2607 | 0 | 0.63861 | 138.8139 | -0.0049421 | 1.9158 | 6.9407 | -0.014826 | 8.8417 |  | 12.8417 | 4 | 12.8417 | 55.2607 | 27.6303 | 20 | 20 | 7.6303 | -971.4938
212 | 3.5333 | 1.802 | 9.7664 | 2 | 10.4 | 55.3647 | 0 | 0.63364 | 139.4475 | -0.0049767 | 1.9009 | 6.9724 | -0.01493 | 8.8584 |  | 12.8584 | 4 | 12.8584 | 55.3647 | 27.6824 | 20 | 20 | 7.6824 | -963.8114
213 | 3.55 | 1.8036 | 9.7714 | 2 | 10.4 | 55.4666 | 0 | 0.62863 | 140.0761 | -0.0050107 | 1.8859 | 7.0038 | -0.015032 | 8.8747 |  | 12.8747 | 4 | 12.8747 | 55.4666 | 27.7333 | 20 | 20 | 7.7333 | -956.0781
214 | 3.5667 | 1.8051 | 9.7764 | 2 | 10.4 | 55.5663 | 0 | 0.62358 | 140.6997 | -0.0050439 | 1.8707 | 7.035 | -0.015132 | 8.8906 |  | 12.8906 | 4 | 12.8906 | 55.5663 | 27.7831 | 20 | 20 | 7.7831 | -948.295
215 | 3.5833 | 1.8067 | 9.7815 | 2 | 10.4 | 55.6637 | 0 | 0.61851 | 141.3182 | -0.0050764 | 1.8555 | 7.0659 | -0.015229 | 8.9062 |  | 12.9062 | 4 | 12.9062 | 55.6637 | 27.8319 | 20 | 20 | 7.8319 | -940.4632
216 | 3.6 | 1.8083 | 9.7866 | 2 | 10.4 | 55.7591 | 0 | 0.6134 | 141.9316 | -0.0051082 | 1.8402 | 7.0966 | -0.015325 | 8.9214 |  | 12.9214 | 4 | 12.9214 | 55.7591 | 27.8795 | 20 | 20 | 7.8795 | -932.5836
217 | 3.6167 | 1.8099 | 9.7917 | 2 | 10.4 | 55.8522 | 0 | 0.60826 | 142.5399 | -0.0051393 | 1.8248 | 7.127 | -0.015418 | 8.9364 |  | 12.9364 | 4 | 12.9364 | 55.8522 | 27.9261 | 20 | 20 | 7.9261 | -924.6575
218 | 3.6333 | 1.8115 | 9.7969 | 2 | 10.4 | 55.9432 | 0 | 0.60309 | 143.143 | -0.0051696 | 1.8093 | 7.1571 | -0.015509 | 8.9509 |  | 12.9509 | 4 | 12.9509 | 55.9432 | 27.9716 | 20 | 20 | 7.9716 | -916.6859
219 | 3.65 | 1.8132 | 9.8021 | 2 | 10.4 | 56.032 | 0 | 0.59789 | 143.7408 | -0.0051993 | 1.7937 | 7.187 | -0.015598 | 8.9651 |  | 12.9651 | 4 | 12.9651 | 56.032 | 28.016 | 20 | 20 | 8.016 | -908.67
220 | 3.6667 | 1.8148 | 9.8073 | 2 | 10.4 | 56.1186 | 0 | 0.59266 | 144.3335 | -0.0052283 | 1.778 | 7.2167 | -0.015685 | 8.979 |  | 12.979 | 4 | 12.979 | 56.1186 | 28.0593 | 20 | 20 | 8.0593 | -900.6107
221 | 3.6833 | 1.8164 | 9.8126 | 2 | 10.4 | 56.2031 | 0 | 0.5874 | 144.9209 | -0.0052565 | 1.7622 | 7.246 | -0.01577 | 8.9925 |  | 12.9925 | 4 | 12.9925 | 56.2031 | 28.1015 | 20 | 20 | 8.1015 | -892.5091
222 | 3.7 | 1.8181 | 9.8179 | 2 | 10.4 | 56.2854 | 0 | 0.58212 | 145.503 | -0.0052841 | 1.7464 | 7.2752 | -0.015852 | 9.0057 |  | 13.0057 | 4 | 13.0057 | 56.2854 | 28.1427 | 20 | 20 | 8.1427 | -884.3665
223 | 3.7167 | 1.8197 | 9.8232 | 2 | 10.4 | 56.3656 | 0 | 0.57681 | 146.0798 | -0.0053109 | 1.7304 | 7.304 | -0.015933 | 9.0185 |  | 13.0185 | 4 | 13.0185 | 56.3656 | 28.1828 | 20 | 20 | 8.1828 | -876.1837
224 | 3.7333 | 1.8214 | 9.8285 | 2 | 10.4 | 56.4436 | 0 | 0.57147 | 146.6513 | -0.005337 | 1.7144 | 7.3326 | -0.016011 | 9.031 |  | 13.031 | 4 | 13.031 | 56.4436 | 28.2218 | 20 | 20 | 8.2218 | -867.9619
225 | 3.75 | 1.8231 | 9.8339 | 2 | 10.4 | 56.5195 | 0 | 0.56611 | 147.2174 | -0.0053625 | 1.6983 | 7.3609 | -0.016087 | 9.0431 |  | 13.0431 | 4 | 13.0431 | 56.5195 | 28.2597 | 20 | 20 | 8.2597 | -859.7022
226 | 3.7667 | 1.8248 | 9.8393 | 2 | 10.4 | 56.5932 | 0 | 0.56072 | 147.7781 | -0.0053872 | 1.6822 | 7.3889 | -0.016162 | 9.0549 |  | 13.0549 | 4 | 13.0549 | 56.5932 | 28.2966 | 20 | 20 | 8.2966 | -851.4055
227 | 3.7833 | 1.8265 | 9.8447 | 2 | 10.4 | 56.6648 | 0 | 0.55531 | 148.3335 | -0.0054113 | 1.6659 | 7.4167 | -0.016234 | 9.0664 |  | 13.0664 | 4 | 13.0664 | 56.6648 | 28.3324 | 20 | 20 | 8.3324 | -843.0731
228 | 3.8 | 1.8282 | 9.8501 | 2 | 10.4 | 56.7343 | 0 | 0.54988 | 148.8833 | -0.0054346 | 1.6496 | 7.4442 | -0.016304 | 9.0775 |  | 13.0775 | 4 | 13.0775 | 56.7343 | 28.3672 | 20 | 20 | 8.3672 | -834.706
229 | 3.8167 | 1.8299 | 9.8556 | 2 | 10.4 | 56.8017 | 0 | 0.54442 | 149.4278 | -0.0054573 | 1.6333 | 7.4714 | -0.016372 | 9.0883 |  | 13.0883 | 4 | 13.0883 | 56.8017 | 28.4009 | 20 | 20 | 8.4009 | -826.3051
230 | 3.8333 | 1.8316 | 9.8611 | 2 | 10.4 | 56.867 | 0 | 0.53894 | 149.9667 | -0.0054793 | 1.6168 | 7.4983 | -0.016438 | 9.0987 |  | 13.0987 | 4 | 13.0987 | 56.867 | 28.4335 | 20 | 20 | 8.4335 | -817.8716
231 | 3.85 | 1.8333 | 9.8666 | 2 | 10.4 | 56.9302 | 0 | 0.53344 | 150.5001 | -0.0055006 | 1.6003 | 7.525 | -0.016502 | 9.1088 |  | 13.1088 | 4 | 13.1088 | 56.9302 | 28.4651 | 20 | 20 | 8.4651 | -809.4065
232 | 3.8667 | 1.835 | 9.8721 | 2 | 10.4 | 56.9912 | 0 | 0.52792 | 151.0281 | -0.0055212 | 1.5838 | 7.5514 | -0.016564 | 9.1186 |  | 13.1186 | 4 | 13.1186 | 56.9912 | 28.4956 | 20 | 20 | 8.4956 | -800.9109
233 | 3.8833 | 1.8368 | 9.8776 | 2 | 10.4 | 57.0502 | 0 | 0.52238 | 151.5504 | -0.0055411 | 1.5671 | 7.5775 | -0.016623 | 9.128 |  | 13.128 | 4 | 13.128 | 57.0502 | 28.5251 | 20 | 20 | 8.5251 | -792.3858
234 | 3.9 | 1.8385 | 9.8832 | 2 | 10.4 | 57.1071 | 0 | 0.51682 | 152.0673 | -0.0055603 | 1.5505 | 7.6034 | -0.016681 | 9.1371 |  | 13.1371 | 4 | 13.1371 | 57.1071 | 28.5535 | 20 | 20 | 8.5535 | -783.8323
235 | 3.9167 | 1.8402 | 9.8888 | 2 | 10.4 | 57.1619 | 0 | 0.51124 | 152.5785 | -0.0055789 | 1.5337 | 7.6289 | -0.016737 | 9.1459 |  | 13.1459 | 4 | 13.1459 | 57.1619 | 28.5809 | 20 | 20 | 8.5809 | -775.2513
236 | 3.9333 | 1.842 | 9.8944 | 2 | 10.4 | 57.2146 | 0 | 0.50564 | 153.0841 | -0.0055967 | 1.5169 | 7.6542 | -0.01679 | 9.1543 |  | 13.1543 | 4 | 13.1543 | 57.2146 | 28.6073 | 20 | 20 | 8.6073 | -766.644
237 | 3.95 | 1.8437 | 9.9 | 2 | 10.4 | 57.2653 | 0 | 0.50003 | 153.5842 | -0.0056139 | 1.5001 | 7.6792 | -0.016842 | 9.1624 |  | 13.1624 | 4 | 13.1624 | 57.2653 | 28.6327 | 20 | 20 | 8.6327 | -758.0114
238 | 3.9667 | 1.8455 | 9.9056 | 2 | 10.4 | 57.3139 | 0 | 0.4944 | 154.0786 | -0.0056305 | 1.4832 | 7.7039 | -0.016891 | 9.1702 |  | 13.1702 | 4 | 13.1702 | 57.3139 | 28.657 | 20 | 20 | 8.657 | -749.3544
239 | 3.9833 | 1.8473 | 9.9112 | 2 | 10.4 | 57.3605 | 0 | 0.48875 | 154.5673 | -0.0056463 | 1.4663 | 7.7284 | -0.016939 | 9.1777 |  | 13.1777 | 4 | 13.1777 | 57.3605 | 28.6802 | 20 | 20 | 8.6802 | -740.6742
240 | 4 | 1.849 | 9.9169 | 2 | 10.4 | 57.405 | 0 | 0.48309 | 155.0504 | -0.0056615 | 1.4493 | 7.7525 | -0.016985 | 9.1848 |  | 13.1848 | 4 | 13.1848 | 57.405 | 28.7025 | 20 | 20 | 8.7025 | -731.9716
241 | 4.0167 | 1.8508 | 9.9226 | 2 | 10.4 | 57.4475 | 0 | 0.47741 | 155.5278 | -0.005676 | 1.4322 | 7.7764 | -0.017028 | 9.1916 |  | 13.1916 | 4 | 13.1916 | 57.4475 | 28.7238 | 20 | 20 | 8.7238 | -723.2479
242 | 4.0333 | 1.8526 | 9.9283 | 2 | 10.4 | 57.488 | 0 | 0.47172 | 155.9995 | -0.0056899 | 1.4152 | 7.8 | -0.01707 | 9.1981 |  | 13.1981 | 4 | 13.1981 | 57.488 | 28.744 | 20 | 20 | 8.744 | -714.5039
243 | 4.05 | 1.8544 | 9.934 | 2 | 10.4 | 57.5264 | 0 | 0.46602 | 156.4656 | -0.0057031 | 1.3981 | 7.8233 | -0.017109 | 9.2042 |  | 13.2042 | 4 | 13.2042 | 57.5264 | 28.7632 | 20 | 20 | 8.7632 | -705.7407
244 | 4.0667 | 1.8562 | 9.9397 | 2 | 10.4 | 57.5629 | 0 | 0.4603 | 156.9259 | -0.0057156 | 1.3809 | 7.8463 | -0.017147 | 9.2101 |  | 13.2101 | 4 | 13.2101 | 57.5629 | 28.7814 | 20 | 20 | 8.7814 | -696.9592
245 | 4.0833 | 1.8579 | 9.9454 | 2 | 10.4 | 57.5973 | 0 | 0.45458 | 157.3804 | -0.0057275 | 1.3637 | 7.869 | -0.017183 | 9.2156 |  | 13.2156 | 4 | 13.2156 | 57.5973 | 28.7987 | 20 | 20 | 8.7987 | -688.1606
246 | 4.1 | 1.8597 | 9.9512 | 2 | 10.4 | 57.6298 | 0 | 0.44884 | 157.8293 | -0.0057387 | 1.3465 | 7.8915 | -0.017216 | 9.2208 |  | 13.2208 | 4 | 13.2208 | 57.6298 | 28.8149 | 20 | 20 | 8.8149 | -679.3457
247 | 4.1167 | 1.8615 | 9.9569 | 2 | 10.4 | 57.6602 | 0 | 0.44309 | 158.2724 | -0.0057493 | 1.3293 | 7.9136 | -0.017248 | 9.2256 |  | 13.2256 | 4 | 13.2256 | 57.6602 | 28.8301 | 20 | 20 | 8.8301 | -670.5156
248 | 4.1333 | 1.8633 | 9.9627 | 2 | 10.4 | 57.6887 | 0 | 0.43733 | 158.7097 | -0.0057593 | 1.312 | 7.9355 | -0.017278 | 9.2302 |  | 13.2302 | 4 | 13.2302 | 57.6887 | 28.8444 | 20 | 20 | 8.8444 | -661.6712
249 | 4.15 | 1.8651 | 9.9684 | 2 | 10.4 | 57.7153 | 0 | 0.43156 | 159.1413 | -0.0057686 | 1.2947 | 7.9571 | -0.017306 | 9.2344 |  | 13.2344 | 4 | 13.2344 | 57.7153 | 28.8576 | 20 | 20 | 8.8576 | -652.8136
250 | 4.1667 | 1.8669 | 9.9742 | 2 | 10.4 | 57.7398 | 0 | 0.42578 | 159.567 | -0.0057772 | 1.2774 | 7.9784 | -0.017332 | 9.2384 |  | 13.2384 | 4 | 13.2384 | 57.7398 | 28.8699 | 20 | 20 | 8.8699 | -643.9437
251 | 4.1833 | 1.8688 | 9.98 | 2 | 10.4 | 57.7625 | 0 | 0.42 | 159.987 | -0.0057852 | 1.26 | 7.9994 | -0.017356 | 9.242 |  | 13.242 | 4 | 13.242 | 57.7625 | 28.8812 | 20 | 20 | 8.8812 | -635.0624
252 | 4.2 | 1.8706 | 9.9858 | 2 | 10.4 | 57.7831 | 0 | 0.41421 | 160.4012 | -0.0057926 | 1.2426 | 8.0201 | -0.017378 | 9.2453 |  | 13.2453 | 4 | 13.2453 | 57.7831 | 28.8916 | 20 | 20 | 8.8916 | -626.1709
253 | 4.2167 | 1.8724 | 9.9916 | 2 | 10.4 | 57.8019 | 0 | 0.40841 | 160.8097 | -0.0057993 | 1.2252 | 8.0405 | -0.017398 | 9.2483 |  | 13.2483 | 4 | 13.2483 | 57.8019 | 28.901 | 20 | 20 | 8.901 | -617.2699
254 | 4.2333 | 1.8742 | 9.9974 | 2 | 10.4 | 57.8188 | 0 | 0.4026 | 161.2123 | -0.0058055 | 1.2078 | 8.0606 | -0.017416 | 9.251 |  | 13.251 | 4 | 13.251 | 57.8188 | 28.9094 | 20 | 20 | 8.9094 | -608.3605
255 | 4.25 | 1.876 | 10.0032 | 2 | 10.4 | 57.8337 | 0 | 0.39679 | 161.609 | -0.005811 | 1.1904 | 8.0805 | -0.017433 | 9.2534 |  | 13.2534 | 4 | 13.2534 | 57.8337 | 28.9168 | 20 | 20 | 8.9168 | -599.4437
256 | 4.2667 | 1.8778 | 10.009 | 2 | 10.4 | 57.8467 | 0 | 0.39097 | 162 | -0.0058158 | 1.1729 | 8.1 | -0.017447 | 9.2555 |  | 13.2555 | 4 | 13.2555 | 57.8467 | 28.9234 | 20 | 20 | 8.9234 | -590.5203
257 | 4.2833 | 1.8796 | 10.0148 | 2 | 10.4 | 57.8579 | 0 | 0.38515 | 162.3852 | -0.0058201 | 1.1555 | 8.1193 | -0.01746 | 9.2573 |  | 13.2573 | 4 | 13.2573 | 57.8579 | 28.9289 | 20 | 20 | 8.9289 | -581.5914
258 | 4.3 | 1.8815 | 10.0207 | 2 | 10.4 | 57.8672 | 0 | 0.37933 | 162.7645 | -0.0058237 | 1.138 | 8.1382 | -0.017471 | 9.2587 |  | 13.2587 | 4 | 13.2587 | 57.8672 | 28.9336 | 20 | 20 | 8.9336 | -572.6578
259 | 4.3167 | 1.8833 | 10.0265 | 2 | 10.4 | 57.8746 | 0 | 0.3735 | 163.138 | -0.0058267 | 1.1205 | 8.1569 | -0.01748 | 9.2599 |  | 13.2599 | 4 | 13.2599 | 57.8746 | 28.9373 | 20 | 20 | 8.9373 | -563.7205
260 | 4.3333 | 1.8851 | 10.0323 | 2 | 10.4 | 57.8801 | 0 | 0.36768 | 163.5057 | -0.0058292 | 1.103 | 8.1753 | -0.017487 | 9.2608 |  | 13.2608 | 4 | 13.2608 | 57.8801 | 28.9401 | 20 | 20 | 8.9401 | -554.7804
261 | 4.35 | 1.8869 | 10.0382 | 2 | 10.4 | 57.8838 | 0 | 0.36184 | 163.8675 | -0.005831 | 1.0855 | 8.1934 | -0.017493 | 9.2614 |  | 13.2614 | 4 | 13.2614 | 57.8838 | 28.9419 | 20 | 20 | 8.9419 | -545.8385
262 | 4.3667 | 1.8887 | 10.044 | 2 | 10.4 | 57.8857 | 0 | 0.35601 | 164.2235 | -0.0058322 | 1.068 | 8.2112 | -0.017497 | 9.2617 |  | 13.2617 | 4 | 13.2617 | 57.8857 | 28.9429 | 20 | 20 | 8.9429 | -536.8956
263 | 4.3833 | 1.8906 | 10.0498 | 2 | 10.4 | 57.8858 | 0 | 0.35018 | 164.5737 | -0.0058328 | 1.0505 | 8.2287 | -0.017498 | 9.2617 |  | 13.2617 | 4 | 13.2617 | 57.8858 | 28.9429 | 20 | 20 | 8.9429 | -527.9528
264 | 4.4 | 1.8924 | 10.0557 | 2 | 10.4 | 57.884 | 0 | 0.34435 | 164.9181 | -0.0058328 | 1.033 | 8.2459 | -0.017498 | 9.2614 |  | 13.2614 | 4 | 13.2614 | 57.884 | 28.942 | 20 | 20 | 8.942 | -519.0107
265 | 4.4167 | 1.8942 | 10.0615 | 2 | 10.4 | 57.8805 | 0 | 0.33851 | 165.2566 | -0.0058322 | 1.0155 | 8.2628 | -0.017497 | 9.2609 |  | 13.2609 | 4 | 13.2609 | 57.8805 | 28.9402 | 20 | 20 | 8.9402 | -510.0705
266 | 4.4333 | 1.896 | 10.0673 | 2 | 10.4 | 57.8751 | 0 | 0.33268 | 165.5893 | -0.0058311 | 0.99805 | 8.2795 | -0.017493 | 9.26 |  | 13.26 | 4 | 13.26 | 57.8751 | 28.9376 | 20 | 20 | 8.9376 | -501.133
267 | 4.45 | 1.8979 | 10.0731 | 2 | 10.4 | 57.868 | 0 | 0.32685 | 165.9161 | -0.0058293 | 0.98056 | 8.2958 | -0.017488 | 9.2589 |  | 13.2589 | 4 | 13.2589 | 57.868 | 28.934 | 20 | 20 | 8.934 | -492.199
268 | 4.4667 | 1.8997 | 10.079 | 2 | 10.4 | 57.8591 | 0 | 0.32103 | 166.2371 | -0.005827 | 0.96308 | 8.3119 | -0.017481 | 9.2575 |  | 13.2575 | 4 | 13.2575 | 57.8591 | 28.9295 | 20 | 20 | 8.9295 | -483.2694
269 | 4.4833 | 1.9015 | 10.0848 | 2 | 10.4 | 57.8485 | 0 | 0.3152 | 166.5523 | -0.0058241 | 0.94561 | 8.3276 | -0.017472 | 9.2558 |  | 13.2558 | 4 | 13.2558 | 57.8485 | 28.9242 | 20 | 20 | 8.9242 | -474.3452
270 | 4.5 | 1.9033 | 10.0906 | 2 | 10.4 | 57.8361 | 0 | 0.30938 | 166.8617 | -0.0058206 | 0.92815 | 8.3431 | -0.017462 | 9.2538 |  | 13.2538 | 4 | 13.2538 | 57.8361 | 28.918 | 20 | 20 | 8.918 | -465.4272
271 | 4.5167 | 1.9051 | 10.0964 | 2 | 10.4 | 57.8219 | 0 | 0.30357 | 167.1653 | -0.0058166 | 0.9107 | 8.3583 | -0.01745 | 9.2515 |  | 13.2515 | 4 | 13.2515 | 57.8219 | 28.911 | 20 | 20 | 8.911 | -456.5162
272 | 4.5333 | 1.907 | 10.1022 | 2 | 10.4 | 57.8061 | 0 | 0.29775 | 167.463 | -0.005812 | 0.89326 | 8.3732 | -0.017436 | 9.249 |  | 13.249 | 4 | 13.249 | 57.8061 | 28.903 | 20 | 20 | 8.903 | -447.6131
273 | 4.55 | 1.9088 | 10.1081 | 2 | 10.4 | 57.7886 | 0 | 0.29195 | 167.755 | -0.0058068 | 0.87584 | 8.3877 | -0.01742 | 9.2462 |  | 13.2462 | 4 | 13.2462 | 57.7886 | 28.8943 | 20 | 20 | 8.8943 | -438.7189
274 | 4.5667 | 1.9106 | 10.1139 | 2 | 10.4 | 57.7693 | 0 | 0.28615 | 168.0411 | -0.0058011 | 0.85844 | 8.4021 | -0.017403 | 9.2431 |  | 13.2431 | 4 | 13.2431 | 57.7693 | 28.8847 | 20 | 20 | 8.8847 | -429.8342
275 | 4.5833 | 1.9124 | 10.1196 | 2 | 10.4 | 57.7484 | 0 | 0.28035 | 168.3215 | -0.0057948 | 0.84105 | 8.4161 | -0.017384 | 9.2397 |  | 13.2397 | 4 | 13.2397 | 57.7484 | 28.8742 | 20 | 20 | 8.8742 | -420.96
276 | 4.6 | 1.9142 | 10.1254 | 2 | 10.4 | 57.7258 | 0 | 0.27456 | 168.596 | -0.005788 | 0.82369 | 8.4298 | -0.017364 | 9.2361 |  | 13.2361 | 4 | 13.2361 | 57.7258 | 28.8629 | 20 | 20 | 8.8629 | -412.0971
277 | 4.6167 | 1.916 | 10.1312 | 2 | 10.4 | 57.7015 | 0 | 0.26878 | 168.8648 | -0.0057806 | 0.80635 | 8.4432 | -0.017342 | 9.2322 |  | 13.2322 | 4 | 13.2322 | 57.7015 | 28.8508 | 20 | 20 | 8.8508 | -403.2464
278 | 4.6333 | 1.9178 | 10.137 | 2 | 10.4 | 57.6756 | 0 | 0.26301 | 169.1278 | -0.0057727 | 0.78903 | 8.4564 | -0.017318 | 9.2281 |  | 13.2281 | 4 | 13.2281 | 57.6756 | 28.8378 | 20 | 20 | 8.8378 | -394.4085
279 | 4.65 | 1.9196 | 10.1428 | 2 | 10.4 | 57.6481 | 0 | 0.25724 | 169.3851 | -0.0057643 | 0.77173 | 8.4693 | -0.017293 | 9.2237 |  | 13.2237 | 4 | 13.2237 | 57.6481 | 28.824 | 20 | 20 | 8.824 | -385.5845
280 | 4.6667 | 1.9214 | 10.1485 | 2 | 10.4 | 57.6189 | 0 | 0.25149 | 169.6366 | -0.0057553 | 0.75447 | 8.4818 | -0.017266 | 9.219 |  | 13.219 | 4 | 13.219 | 57.6189 | 28.8095 | 20 | 20 | 8.8095 | -376.775
281 | 4.6833 | 1.9232 | 10.1543 | 2 | 10.4 | 57.5882 | 0 | 0.24574 | 169.8823 | -0.0057458 | 0.73723 | 8.4941 | -0.017237 | 9.2141 |  | 13.2141 | 4 | 13.2141 | 57.5882 | 28.7941 | 20 | 20 | 8.7941 | -367.9809
282 | 4.7 | 1.925 | 10.16 | 2 | 10.4 | 57.5558 | 0 | 0.24001 | 170.1223 | -0.0057358 | 0.72002 | 8.5061 | -0.017207 | 9.2089 |  | 13.2089 | 4 | 13.2089 | 57.5558 | 28.7779 | 20 | 20 | 8.7779 | -359.203
283 | 4.7167 | 1.9268 | 10.1657 | 2 | 10.4 | 57.5219 | 0 | 0.23428 | 170.3566 | -0.0057252 | 0.70285 | 8.5178 | -0.017176 | 9.2035 |  | 13.2035 | 4 | 13.2035 | 57.5219 | 28.7609 | 20 | 20 | 8.7609 | -350.4421
284 | 4.7333 | 1.9286 | 10.1714 | 2 | 10.4 | 57.4864 | 0 | 0.22857 | 170.5852 | -0.0057141 | 0.68571 | 8.5293 | -0.017142 | 9.1978 |  | 13.1978 | 4 | 13.1978 | 57.4864 | 28.7432 | 20 | 20 | 8.7432 | -341.6989
285 | 4.75 | 1.9304 | 10.1771 | 2 | 10.4 | 57.4493 | 0 | 0.22287 | 170.808 | -0.0057026 | 0.6686 | 8.5404 | -0.017108 | 9.1919 |  | 13.1919 | 4 | 13.1919 | 57.4493 | 28.7247 | 20 | 20 | 8.7247 | -332.9742
286 | 4.7667 | 1.9321 | 10.1828 | 2 | 10.4 | 57.4107 | 0 | 0.21718 | 171.0252 | -0.0056905 | 0.65153 | 8.5513 | -0.017071 | 9.1857 |  | 13.1857 | 4 | 13.1857 | 57.4107 | 28.7054 | 20 | 20 | 8.7054 | -324.2688
287 | 4.7833 | 1.9339 | 10.1885 | 2 | 10.4 | 57.3706 | 0 | 0.2115 | 171.2367 | -0.0056779 | 0.63449 | 8.5618 | -0.017034 | 9.1793 |  | 13.1793 | 4 | 13.1793 | 57.3706 | 28.6853 | 20 | 20 | 8.6853 | -315.5835
288 | 4.8 | 1.9357 | 10.1942 | 2 | 10.4 | 57.3289 | 0 | 0.20583 | 171.4425 | -0.0056648 | 0.6175 | 8.5721 | -0.016994 | 9.1726 |  | 13.1726 | 4 | 13.1726 | 57.3289 | 28.6645 | 20 | 20 | 8.6645 | -306.9191
289 | 4.8167 | 1.9374 | 10.1998 | 2 | 10.4 | 57.2858 | 0 | 0.20018 | 171.6427 | -0.0056512 | 0.60054 | 8.5821 | -0.016954 | 9.1657 |  | 13.1657 | 4 | 13.1657 | 57.2858 | 28.6429 | 20 | 20 | 8.6429 | -298.2762
290 | 4.8333 | 1.9392 | 10.2055 | 2 | 10.4 | 57.2412 | 0 | 0.19454 | 171.8373 | -0.0056372 | 0.58363 | 8.5919 | -0.016911 | 9.1586 |  | 13.1586 | 4 | 13.1586 | 57.2412 | 28.6206 | 20 | 20 | 8.6206 | -289.6556
291 | 4.85 | 1.941 | 10.2111 | 2 | 10.4 | 57.195 | 0 | 0.18892 | 172.0262 | -0.0056226 | 0.56677 | 8.6013 | -0.016868 | 9.1512 |  | 13.1512 | 4 | 13.1512 | 57.195 | 28.5975 | 20 | 20 | 8.5975 | -281.0581
292 | 4.8667 | 1.9427 | 10.2167 | 2 | 10.4 | 57.1475 | 0 | 0.18331 | 172.2095 | -0.0056076 | 0.54994 | 8.6105 | -0.016823 | 9.1436 |  | 13.1436 | 4 | 13.1436 | 57.1475 | 28.5737 | 20 | 20 | 8.5737 | -272.4843
293 | 4.8833 | 1.9445 | 10.2223 | 2 | 10.4 | 57.0985 | 0 | 0.17772 | 172.3872 | -0.005592 | 0.53317 | 8.6194 | -0.016776 | 9.1358 |  | 13.1358 | 4 | 13.1358 | 57.0985 | 28.5492 | 20 | 20 | 8.5492 | -263.9351
294 | 4.9 | 1.9462 | 10.2279 | 2 | 10.4 | 57.048 | 0 | 0.17215 | 172.5594 | -0.0055761 | 0.51644 | 8.628 | -0.016728 | 9.1277 |  | 13.1277 | 4 | 13.1277 | 57.048 | 28.524 | 20 | 20 | 8.524 | -255.4111
295 | 4.9167 | 1.9479 | 10.2334 | 2 | 10.4 | 56.9961 | 0 | 0.16659 | 172.726 | -0.0055596 | 0.49976 | 8.6363 | -0.016679 | 9.1194 |  | 13.1194 | 4 | 13.1194 | 56.9961 | 28.4981 | 20 | 20 | 8.4981 | -246.9131
296 | 4.9333 | 1.9497 | 10.239 | 2 | 10.4 | 56.9428 | 0 | 0.16104 | 172.887 | -0.0055427 | 0.48313 | 8.6444 | -0.016628 | 9.1109 |  | 13.1109 | 4 | 13.1109 | 56.9428 | 28.4714 | 20 | 20 | 8.4714 | -238.4416
297 | 4.95 | 1.9514 | 10.2445 | 2 | 10.4 | 56.8882 | 0 | 0.15552 | 173.0425 | -0.0055253 | 0.46656 | 8.6521 | -0.016576 | 9.1021 |  | 13.1021 | 4 | 13.1021 | 56.8882 | 28.4441 | 20 | 20 | 8.4441 | -229.9975
298 | 4.9667 | 1.9531 | 10.25 | 2 | 10.4 | 56.8321 | 0 | 0.15001 | 173.1925 | -0.0055075 | 0.45003 | 8.6596 | -0.016522 | 9.0931 |  | 13.0931 | 4 | 13.0931 | 56.8321 | 28.4161 | 20 | 20 | 8.4161 | -221.5815
299 | 4.9833 | 1.9548 | 10.2555 | 2 | 10.4 | 56.7747 | 0 | 0.14452 | 173.3371 | -0.0054892 | 0.43357 | 8.6669 | -0.016468 | 9.084 |  | 13.084 | 4 | 13.084 | 56.7747 | 28.3873 | 20 | 20 | 8.3873 | -213.1941
300 | 5 | 1.9565 | 10.2609 | 2 | 10.4 | 56.7159 | 0 | 0.13905 | 173.4761 | -0.0054705 | 0.41715 | 8.6738 | -0.016411 | 9.0745 |  | 13.0745 | 4 | 13.0745 | 56.7159 | 28.358 | 20 | 20 | 8.358 | -204.8362
301 | 5.0167 | 1.9582 | 10.2664 | 2 | 10.4 | 56.6558 | 0 | 0.1336 | 173.6097 | -0.0054513 | 0.4008 | 8.6805 | -0.016354 | 9.0649 |  | 13.0649 | 4 | 13.0649 | 56.6558 | 28.3279 | 20 | 20 | 8.3279 | -196.5083
302 | 5.0333 | 1.9599 | 10.2718 | 2 | 10.4 | 56.5944 | 0 | 0.12817 | 173.7379 | -0.0054317 | 0.38451 | 8.6869 | -0.016295 | 9.0551 |  | 13.0551 | 4 | 13.0551 | 56.5944 | 28.2972 | 20 | 20 | 8.2972 | -188.2111
303 | 5.05 | 1.9616 | 10.2772 | 2 | 10.4 | 56.5317 | 0 | 0.12276 | 173.8606 | -0.0054117 | 0.36827 | 8.693 | -0.016235 | 9.0451 |  | 13.0451 | 4 | 13.0451 | 56.5317 | 28.2658 | 20 | 20 | 8.2658 | -179.9452
304 | 5.0667 | 1.9633 | 10.2826 | 2 | 10.4 | 56.4676 | 0 | 0.11737 | 173.978 | -0.0053912 | 0.3521 | 8.6989 | -0.016174 | 9.0348 |  | 13.0348 | 4 | 13.0348 | 56.4676 | 28.2338 | 20 | 20 | 8.2338 | -171.7114
305 | 5.0833 | 1.965 | 10.288 | 2 | 10.4 | 56.4023 | 0 | 0.112 | 174.09 | -0.0053703 | 0.33599 | 8.7045 | -0.016111 | 9.0244 |  | 13.0244 | 4 | 13.0244 | 56.4023 | 28.2012 | 20 | 20 | 8.2012 | -163.5102
306 | 5.1 | 1.9667 | 10.2934 | 2 | 10.4 | 56.3358 | 0 | 0.10665 | 174.1966 | -0.005349 | 0.31994 | 8.7098 | -0.016047 | 9.0137 |  | 13.0137 | 4 | 13.0137 | 56.3358 | 28.1679 | 20 | 20 | 8.1679 | -155.3424
307 | 5.1167 | 1.9683 | 10.2987 | 2 | 10.4 | 56.268 | 0 | 0.10132 | 174.298 | -0.0053273 | 0.30396 | 8.7149 | -0.015982 | 9.0029 |  | 13.0029 | 4 | 13.0029 | 56.268 | 28.134 | 20 | 20 | 8.134 | -147.2084
308 | 5.1333 | 1.97 | 10.304 | 2 | 10.4 | 56.1989 | 0 | 0.096014 | 174.394 | -0.0053052 | 0.28804 | 8.7197 | -0.015916 | 8.9918 |  | 12.9918 | 4 | 12.9918 | 56.1989 | 28.0995 | 20 | 20 | 8.0995 | -139.1089
309 | 5.15 | 1.9716 | 10.3093 | 2 | 10.4 | 56.1286 | 0 | 0.090731 | 174.4847 | -0.0052827 | 0.27219 | 8.7242 | -0.015848 | 8.9806 |  | 12.9806 | 4 | 12.9806 | 56.1286 | 28.0643 | 20 | 20 | 8.0643 | -131.0446
310 | 5.1667 | 1.9733 | 10.3145 | 2 | 10.4 | 56.0571 | 0 | 0.085471 | 174.5702 | -0.0052598 | 0.25641 | 8.7285 | -0.015779 | 8.9691 |  | 12.9691 | 4 | 12.9691 | 56.0571 | 28.0286 | 20 | 20 | 8.0286 | -123.016
311 | 5.1833 | 1.9749 | 10.3198 | 2 | 10.4 | 55.9845 | 0 | 0.080235 | 174.6504 | -0.0052365 | 0.2407 | 8.7325 | -0.015709 | 8.9575 |  | 12.9575 | 4 | 12.9575 | 55.9845 | 27.9922 | 20 | 20 | 7.9922 | -115.0238
312 | 5.2 | 1.9766 | 10.325 | 2 | 10.4 | 55.9106 | 0 | 0.075022 | 174.7254 | -0.0052128 | 0.22507 | 8.7363 | -0.015638 | 8.9457 |  | 12.9457 | 4 | 12.9457 | 55.9106 | 27.9553 | 20 | 20 | 7.9553 | -107.0685
313 | 5.2167 | 1.9782 | 10.3302 | 2 | 10.4 | 55.8356 | 0 | 0.069833 | 174.7953 | -0.0051887 | 0.2095 | 8.7398 | -0.015566 | 8.9337 |  | 12.9337 | 4 | 12.9337 | 55.8356 | 27.9178 | 20 | 20 | 7.9178 | -99.1507
314 | 5.2333 | 1.9798 | 10.3353 | 2 | 10.4 | 55.7594 | 0 | 0.064669 | 174.8599 | -0.0051642 | 0.19401 | 8.743 | -0.015493 | 8.9215 |  | 12.9215 | 4 | 12.9215 | 55.7594 | 27.8797 | 20 | 20 | 7.8797 | -91.271
315 | 5.25 | 1.9814 | 10.3405 | 2 | 10.4 | 55.6822 | 0 | 0.05953 | 174.9195 | -0.0051394 | 0.17859 | 8.746 | -0.015418 | 8.9091 |  | 12.9091 | 4 | 12.9091 | 55.6822 | 27.8411 | 20 | 20 | 7.8411 | -83.4299
316 | 5.2667 | 1.983 | 10.3456 | 2 | 10.4 | 55.6037 | 0 | 0.054415 | 174.9739 | -0.0051142 | 0.16325 | 8.7487 | -0.015343 | 8.8966 |  | 12.8966 | 4 | 12.8966 | 55.6037 | 27.8019 | 20 | 20 | 7.8019 | -75.628
317 | 5.2833 | 1.9846 | 10.3507 | 2 | 10.4 | 55.5242 | 0 | 0.049327 | 175.0232 | -0.0050886 | 0.14798 | 8.7512 | -0.015266 | 8.8839 |  | 12.8839 | 4 | 12.8839 | 55.5242 | 27.7621 | 20 | 20 | 7.7621 | -67.8659
318 | 5.3 | 1.9862 | 10.3557 | 2 | 10.4 | 55.4436 | 0 | 0.044264 | 175.0675 | -0.0050627 | 0.13279 | 8.7534 | -0.015188 | 8.871 |  | 12.871 | 4 | 12.871 | 55.4436 | 27.7218 | 20 | 20 | 7.7218 | -60.1441
319 | 5.3167 | 1.9877 | 10.3608 | 2 | 10.4 | 55.3619 | 0 | 0.039228 | 175.1067 | -0.0050364 | 0.11768 | 8.7553 | -0.015109 | 8.8579 |  | 12.8579 | 4 | 12.8579 | 55.3619 | 27.681 | 20 | 20 | 7.681 | -52.4631
320 | 5.3333 | 1.9893 | 10.3658 | 2 | 10.4 | 55.2792 | 0 | 0.034218 | 175.1409 | -0.0050098 | 0.10265 | 8.757 | -0.015029 | 8.8447 |  | 12.8447 | 4 | 12.8447 | 55.2792 | 27.6396 | 20 | 20 | 7.6396 | -44.8235
321 | 5.35 | 1.9909 | 10.3708 | 2 | 10.4 | 55.1954 | 0 | 0.029235 | 175.1702 | -0.0049828 | 0.087706 | 8.7585 | -0.014948 | 8.8313 |  | 12.8313 | 4 | 12.8313 | 55.1954 | 27.5977 | 20 | 20 | 7.5977 | -37.2258
322 | 5.3667 | 1.9924 | 10.3757 | 2 | 10.4 | 55.1106 | 0 | 0.02428 | 175.1944 | -0.0049554 | 0.072839 | 8.7597 | -0.014866 | 8.8177 |  | 12.8177 | 4 | 12.8177 | 55.1106 | 27.5553 | 20 | 20 | 7.5553 | -29.6705
323 | 5.3833 | 1.994 | 10.3806 | 2 | 10.4 | 55.0248 | 0 | 0.019352 | 175.2138 | -0.0049278 | 0.058056 | 8.7607 | -0.014783 | 8.804 |  | 12.804 | 4 | 12.804 | 55.0248 | 27.5124 | 20 | 20 | 7.5124 | -22.1582
324 | 5.4 | 1.9955 | 10.3855 | 2 | 10.4 | 54.9379 | 0 | 0.014452 | 175.2282 | -0.0048998 | 0.043357 | 8.7614 | -0.014699 | 8.7901 |  | 12.7901 | 4 | 12.7901 | 54.9379 | 27.469 | 20 | 20 | 7.469 | -14.6892
325 | 5.4167 | 1.997 | 10.3904 | 2 | 10.4 | 54.8501 | 0 | 0.0095807 | 175.2378 | -0.0048715 | 0.028742 | 8.7619 | -0.014614 | 8.776 |  | 12.776 | 4 | 12.776 | 54.8501 | 27.4251 | 20 | 20 | 7.4251 | -7.2641
326 | 5.4333 | 1.9985 | 10.3953 | 2 | 10.4 | 54.7613 | 0 | 0.0047379 | 175.2426 | -0.0048428 | 0.014214 | 8.7621 | -0.014529 | 8.7618 |  | 12.7618 | 4 | 12.7618 | 54.7613 | 27.3807 | 20 | 20 | 7.3807 | 0.11652
327 | 5.45 | 2 | 10.4001 | 2 | 10.4 | 54.6716 | 0 | -7.6001e-05 | 175.2425 | -0.0048139 | -0.000228 | 8.7621 | -0.014442 | 8.7475 |  | 12.7475 | 4 | 12.7475 | 54.6716 | 27.3358 | 20 | 20 | 7.3358 | 7.4523
328 | 5.4667 | 2.0015 | 10.4049 | 2 | 10.4 | 54.5809 | 0 | -0.0048606 | 175.2376 | -0.0047846 | -0.014582 | 8.7619 | -0.014354 | 8.7329 |  | 12.7329 | 4 | 12.7329 | 54.5809 | 27.2905 | 20 | 20 | 7.2905 | 14.7428
329 | 5.4833 | 2.003 | 10.4096 | 2 | 10.4 | 54.4893 | 0 | -0.0096157 | 175.228 | -0.004755 | -0.028847 | 8.7614 | -0.014265 | 8.7183 |  | 12.7183 | 4 | 12.7183 | 54.4893 | 27.2447 | 20 | 20 | 7.2447 | 21.9874
330 | 5.5 | 2.0045 | 10.4143 | 2 | 10.4 | 54.3968 | 0 | -0.014341 | 175.2137 | -0.0047252 | -0.043023 | 8.7607 | -0.014176 | 8.7035 |  | 12.7035 | 4 | 12.7035 | 54.3968 | 27.1984 | 20 | 20 | 7.1984 | 29.1858
331 | 5.5167 | 2.0059 | 10.419 | 2 | 10.4 | 54.3034 | 0 | -0.019036 | 175.1946 | -0.004695 | -0.057108 | 8.7597 | -0.014085 | 8.6885 |  | 12.6885 | 4 | 12.6885 | 54.3034 | 27.1517 | 20 | 20 | 7.1517 | 36.3375
332 | 5.5333 | 2.0074 | 10.4237 | 2 | 10.4 | 54.2091 | 0 | -0.0237 | 175.1709 | -0.0046645 | -0.071101 | 8.7585 | -0.013994 | 8.6735 |  | 12.6735 | 4 | 12.6735 | 54.2091 | 27.1045 | 20 | 20 | 7.1045 | 43.442
333 | 5.55 | 2.0089 | 10.4283 | 2 | 10.4 | 54.1139 | 0 | -0.028334 | 175.1426 | -0.0046338 | -0.085003 | 8.7571 | -0.013901 | 8.6582 |  | 12.6582 | 4 | 12.6582 | 54.1139 | 27.057 | 20 | 20 | 7.057 | 50.499
334 | 5.5667 | 2.0103 | 10.4329 | 2 | 10.4 | 54.0179 | 0 | -0.032937 | 175.1097 | -0.0046028 | -0.098811 | 8.7555 | -0.013808 | 8.6429 |  | 12.6429 | 4 | 12.6429 | 54.0179 | 27.0089 | 20 | 20 | 7.0089 | 57.5079
335 | 5.5833 | 2.0117 | 10.4375 | 2 | 10.4 | 53.9211 | 0 | -0.037508 | 175.0721 | -0.0045714 | -0.11253 | 8.7536 | -0.013714 | 8.6274 |  | 12.6274 | 4 | 12.6274 | 53.9211 | 26.9605 | 20 | 20 | 6.9605 | 64.4685
336 | 5.6 | 2.0131 | 10.442 | 2 | 10.4 | 53.8234 | 0 | -0.042048 | 175.0301 | -0.0045399 | -0.12614 | 8.7515 | -0.01362 | 8.6117 |  | 12.6117 | 4 | 12.6117 | 53.8234 | 26.9117 | 20 | 20 | 6.9117 | 71.3802
337 | 5.6167 | 2.0145 | 10.4466 | 2 | 10.4 | 53.7249 | 0 | -0.046556 | 174.9835 | -0.004508 | -0.13967 | 8.7492 | -0.013524 | 8.596 |  | 12.596 | 4 | 12.596 | 53.7249 | 26.8625 | 20 | 20 | 6.8625 | 78.2426
338 | 5.6333 | 2.0159 | 10.451 | 2 | 10.4 | 53.6256 | 0 | -0.051032 | 174.9325 | -0.0044759 | -0.1531 | 8.7466 | -0.013428 | 8.5801 |  | 12.5801 | 4 | 12.5801 | 53.6256 | 26.8128 | 20 | 20 | 6.8128 | 85.0554
339 | 5.65 | 2.0173 | 10.4555 | 2 | 10.4 | 53.5256 | 0 | -0.055476 | 174.877 | -0.0044435 | -0.16643 | 8.7439 | -0.013331 | 8.5641 |  | 12.5641 | 4 | 12.5641 | 53.5256 | 26.7628 | 20 | 20 | 6.7628 | 91.8182
340 | 5.6667 | 2.0187 | 10.4599 | 2 | 10.4 | 53.4248 | 0 | -0.059887 | 174.8172 | -0.0044109 | -0.17966 | 8.7409 | -0.013233 | 8.548 |  | 12.548 | 4 | 12.548 | 53.4248 | 26.7124 | 20 | 20 | 6.7124 | 98.5306
341 | 5.6833 | 2.0201 | 10.4643 | 2 | 10.4 | 53.3232 | 0 | -0.064265 | 174.7529 | -0.004378 | -0.19279 | 8.7376 | -0.013134 | 8.5317 |  | 12.5317 | 4 | 12.5317 | 53.3232 | 26.6616 | 20 | 20 | 6.6616 | 105.1922
342 | 5.7 | 2.0214 | 10.4686 | 2 | 10.4 | 53.2209 | 0 | -0.068609 | 174.6843 | -0.0043449 | -0.20583 | 8.7342 | -0.013035 | 8.5154 |  | 12.5154 | 4 | 12.5154 | 53.2209 | 26.6105 | 20 | 20 | 6.6105 | 111.8027
343 | 5.7167 | 2.0228 | 10.4729 | 2 | 10.4 | 53.1179 | 0 | -0.072921 | 174.6114 | -0.0043115 | -0.21876 | 8.7306 | -0.012935 | 8.4989 |  | 12.4989 | 4 | 12.4989 | 53.1179 | 26.559 | 20 | 20 | 6.559 | 118.3617
344 | 5.7333 | 2.0241 | 10.4772 | 2 | 10.4 | 53.0142 | 0 | -0.077199 | 174.5342 | -0.004278 | -0.2316 | 8.7267 | -0.012834 | 8.4823 |  | 12.4823 | 4 | 12.4823 | 53.0142 | 26.5071 | 20 | 20 | 6.5071 | 124.8688
345 | 5.75 | 2.0255 | 10.4814 | 2 | 10.4 | 52.9098 | 0 | -0.081443 | 174.4527 | -0.0042441 | -0.24433 | 8.7226 | -0.012732 | 8.4656 |  | 12.4656 | 4 | 12.4656 | 52.9098 | 26.4549 | 20 | 20 | 6.4549 | 131.3237
346 | 5.7667 | 2.0268 | 10.4857 | 2 | 10.4 | 52.8048 | 0 | -0.085653 | 174.3671 | -0.0042101 | -0.25696 | 8.7184 | -0.01263 | 8.4488 |  | 12.4488 | 4 | 12.4488 | 52.8048 | 26.4024 | 20 | 20 | 6.4024 | 137.7261
347 | 5.7833 | 2.0281 | 10.4898 | 2 | 10.4 | 52.699 | 0 | -0.089829 | 174.2772 | -0.0041758 | -0.26949 | 8.7139 | -0.012527 | 8.4318 |  | 12.4318 | 4 | 12.4318 | 52.699 | 26.3495 | 20 | 20 | 6.3495 | 144.0756
348 | 5.8 | 2.0294 | 10.494 | 2 | 10.4 | 52.5927 | 0 | -0.09397 | 174.1833 | -0.0041413 | -0.28191 | 8.7092 | -0.012424 | 8.4148 |  | 12.4148 | 4 | 12.4148 | 52.5927 | 26.2963 | 20 | 20 | 6.2963 | 150.3719
349 | 5.8167 | 2.0306 | 10.4981 | 2 | 10.4 | 52.4857 | 0 | -0.098077 | 174.0852 | -0.0041067 | -0.29423 | 8.7043 | -0.01232 | 8.3977 |  | 12.3977 | 4 | 12.3977 | 52.4857 | 26.2428 | 20 | 20 | 6.2428 | 156.6148
350 | 5.8333 | 2.0319 | 10.5021 | 2 | 10.4 | 52.3781 | 0 | -0.10215 | 173.983 | -0.0040718 | -0.30645 | 8.6992 | -0.012215 | 8.3805 |  | 12.3805 | 4 | 12.3805 | 52.3781 | 26.189 | 20 | 20 | 6.189 | 162.8038
351 | 5.85 | 2.0332 | 10.5062 | 2 | 10.4 | 52.2699 | 0 | -0.10619 | 173.8768 | -0.0040367 | -0.31856 | 8.6938 | -0.01211 | 8.3632 |  | 12.3632 | 4 | 12.3632 | 52.2699 | 26.1349 | 20 | 20 | 6.1349 | 168.9387
352 | 5.8667 | 2.0344 | 10.5102 | 2 | 10.4 | 52.1611 | 0 | -0.11019 | 173.7667 | -0.0040014 | -0.33056 | 8.6883 | -0.012004 | 8.3458 |  | 12.3458 | 4 | 12.3458 | 52.1611 | 26.0805 | 20 | 20 | 6.0805 | 175.0193
353 | 5.8833 | 2.0357 | 10.5142 | 2 | 10.4 | 52.0517 | 0 | -0.11415 | 173.6525 | -0.0039659 | -0.34246 | 8.6826 | -0.011898 | 8.3283 |  | 12.3283 | 4 | 12.3283 | 52.0517 | 26.0258 | 20 | 20 | 6.0258 | 181.0451
354 | 5.9 | 2.0369 | 10.5181 | 2 | 10.4 | 51.9418 | 0 | -0.11808 | 173.5344 | -0.0039302 | -0.35425 | 8.6767 | -0.011791 | 8.3107 |  | 12.3107 | 4 | 12.3107 | 51.9418 | 25.9709 | 20 | 20 | 5.9709 | 187.016
355 | 5.9167 | 2.0381 | 10.522 | 2 | 10.4 | 51.8313 | 0 | -0.12198 | 173.4124 | -0.0038944 | -0.36593 | 8.6706 | -0.011683 | 8.293 |  | 12.293 | 4 | 12.293 | 51.8313 | 25.9156 | 20 | 20 | 5.9156 | 192.9316
356 | 5.9333 | 2.0393 | 10.5258 | 2 | 10.4 | 51.7203 | 0 | -0.12584 | 173.2866 | -0.0038584 | -0.37751 | 8.6643 | -0.011575 | 8.2752 |  | 12.2752 | 4 | 12.2752 | 51.7203 | 25.8602 | 20 | 20 | 5.8602 | 198.7918
357 | 5.95 | 2.0405 | 10.5297 | 2 | 10.4 | 51.6088 | 0 | -0.12966 | 173.157 | -0.0038222 | -0.38897 | 8.6578 | -0.011466 | 8.2574 |  | 12.2574 | 4 | 12.2574 | 51.6088 | 25.8044 | 20 | 20 | 5.8044 | 204.5962
358 | 5.9667 | 2.0417 | 10.5334 | 2 | 10.4 | 51.4968 | 0 | -0.13344 | 173.0235 | -0.0037858 | -0.40033 | 8.6512 | -0.011357 | 8.2395 |  | 12.2395 | 4 | 12.2395 | 51.4968 | 25.7484 | 20 | 20 | 5.7484 | 210.3446
359 | 5.9833 | 2.0429 | 10.5372 | 2 | 10.4 | 51.3843 | 0 | -0.13719 | 172.8863 | -0.0037493 | -0.41158 | 8.6443 | -0.011248 | 8.2215 |  | 12.2215 | 4 | 12.2215 | 51.3843 | 25.6922 | 20 | 20 | 5.6922 | 216.0367
360 | 6 | 2.044 | 10.5409 | 2 | 10.4 | 51.2714 | 0 | -0.14091 | 172.7454 | -0.0037126 | -0.42272 | 8.6373 | -0.011138 | 8.2034 |  | 12.2034 | 4 | 12.2034 | 51.2714 | 25.6357 | 20 | 20 | 5.6357 | 221.6724
361 | 6.0167 | 2.0452 | 10.5446 | 2 | 10.4 | 51.1579 | 0 | -0.14458 | 172.6008 | -0.0036758 | -0.43374 | 8.63 | -0.011027 | 8.1853 |  | 12.1853 | 4 | 12.1853 | 51.1579 | 25.579 | 20 | 20 | 5.579 | 227.2514
362 | 6.0333 | 2.0463 | 10.5482 | 2 | 10.4 | 51.0441 | 0 | -0.14822 | 172.4526 | -0.0036388 | -0.44466 | 8.6226 | -0.010916 | 8.1671 |  | 12.1671 | 4 | 12.1671 | 51.0441 | 25.522 | 20 | 20 | 5.522 | 232.7734
363 | 6.05 | 2.0474 | 10.5518 | 2 | 10.4 | 50.9298 | 0 | -0.15182 | 172.3008 | -0.0036016 | -0.45546 | 8.615 | -0.010805 | 8.1488 |  | 12.1488 | 4 | 12.1488 | 50.9298 | 25.4649 | 20 | 20 | 5.4649 | 238.2383
364 | 6.0667 | 2.0486 | 10.5554 | 2 | 10.4 | 50.8151 | 0 | -0.15539 | 172.1454 | -0.0035644 | -0.46616 | 8.6073 | -0.010693 | 8.1304 |  | 12.1304 | 4 | 12.1304 | 50.8151 | 25.4076 | 20 | 20 | 5.4076 | 243.6459
365 | 6.0833 | 2.0497 | 10.5589 | 2 | 10.4 | 50.7 | 0 | -0.15891 | 171.9865 | -0.003527 | -0.47674 | 8.5993 | -0.010581 | 8.112 |  | 12.112 | 4 | 12.112 | 50.7 | 25.35 | 20 | 20 | 5.35 | 248.9959
366 | 6.1 | 2.0508 | 10.5624 | 2 | 10.4 | 50.5846 | 0 | -0.1624 | 171.8241 | -0.0034894 | -0.48721 | 8.5912 | -0.010468 | 8.0935 |  | 12.0935 | 4 | 12.0935 | 50.5846 | 25.2923 | 20 | 20 | 5.2923 | 254.2882
367 | 6.1167 | 2.0518 | 10.5659 | 2 | 10.4 | 50.4687 | 0 | -0.16585 | 171.6582 | -0.0034518 | -0.49756 | 8.5829 | -0.010355 | 8.075 |  | 12.075 | 4 | 12.075 | 50.4687 | 25.2344 | 20 | 20 | 5.2344 | 259.5225
368 | 6.1333 | 2.0529 | 10.5693 | 2 | 10.4 | 50.3525 | 0 | -0.16927 | 171.489 | -0.003414 | -0.5078 | 8.5744 | -0.010242 | 8.0564 |  | 12.0564 | 4 | 12.0564 | 50.3525 | 25.1763 | 20 | 20 | 5.1763 | 264.6988
369 | 6.15 | 2.054 | 10.5726 | 2 | 10.4 | 50.236 | 0 | -0.17264 | 171.3163 | -0.0033761 | -0.51793 | 8.5658 | -0.010128 | 8.0378 |  | 12.0378 | 4 | 12.0378 | 50.236 | 25.118 | 20 | 20 | 5.118 | 269.8168
370 | 6.1667 | 2.055 | 10.576 | 2 | 10.4 | 50.1191 | 0 | -0.17598 | 171.1403 | -0.0033381 | -0.52795 | 8.557 | -0.010014 | 8.0191 |  | 12.0191 | 4 | 12.0191 | 50.1191 | 25.0595 | 20 | 20 | 5.0595 | 274.8763
371 | 6.1833 | 2.056 | 10.5793 | 2 | 10.4 | 50.0019 | 0 | -0.17928 | 170.9611 | -0.0033 | -0.53785 | 8.5481 | -0.0099 | 8.0003 |  | 12.0003 | 4 | 12.0003 | 50.0019 | 25.001 | 20 | 20 | 5.001 | 279.8773
372 | 6.2 | 2.057 | 10.5825 | 2 | 10.4 | 49.8844 | 0 | -0.18254 | 170.7785 | -0.0032618 | -0.54763 | 8.5389 | -0.0097853 | 7.9815 |  | 11.9815 | 4 | 11.9815 | 49.8844 | 24.9422 | 20 | 20 | 4.9422 | 284.8195
373 | 6.2167 | 2.0581 | 10.5858 | 2 | 10.4 | 49.7667 | 0 | -0.18577 | 170.5927 | -0.0032235 | -0.5573 | 8.5296 | -0.0096704 | 7.9627 |  | 11.9627 | 4 | 11.9627 | 49.7667 | 24.8833 | 20 | 20 | 4.8833 | 289.7028
374 | 6.2333 | 2.059 | 10.589 | 2 | 10.4 | 49.6486 | 0 | -0.18895 | 170.4038 | -0.003185 | -0.56686 | 8.5202 | -0.0095551 | 7.9438 |  | 11.9438 | 4 | 11.9438 | 49.6486 | 24.8243 | 20 | 20 | 4.8243 | 294.5271
375 | 6.25 | 2.06 | 10.5921 | 2 | 10.4 | 49.5303 | 0 | -0.1921 | 170.2117 | -0.0031466 | -0.5763 | 8.5106 | -0.0094397 | 7.9248 |  | 11.9248 | 4 | 11.9248 | 49.5303 | 24.7651 | 20 | 20 | 4.7651 | 299.2923
376 | 6.2667 | 2.061 | 10.5952 | 2 | 10.4 | 49.4117 | 0 | -0.19521 | 170.0165 | -0.003108 | -0.58562 | 8.5008 | -0.0093239 | 7.9059 |  | 11.9059 | 4 | 11.9059 | 49.4117 | 24.7059 | 20 | 20 | 4.7059 | 303.9982
377 | 6.2833 | 2.062 | 10.5983 | 2 | 10.4 | 49.293 | 0 | -0.19828 | 169.8182 | -0.0030693 | -0.59483 | 8.4909 | -0.0092079 | 7.8869 |  | 11.8869 | 4 | 11.8869 | 49.293 | 24.6465 | 20 | 20 | 4.6465 | 308.6446
378 | 6.3 | 2.0629 | 10.6013 | 2 | 10.4 | 49.174 | 0 | -0.20131 | 169.6169 | -0.0030306 | -0.60392 | 8.4808 | -0.0090917 | 7.8678 |  | 11.8678 | 4 | 11.8678 | 49.174 | 24.587 | 20 | 20 | 4.587 | 313.2316
379 | 6.3167 | 2.0638 | 10.6043 | 2 | 10.4 | 49.0547 | 0 | -0.2043 | 169.4126 | -0.0029918 | -0.6129 | 8.4706 | -0.0089753 | 7.8488 |  | 11.8488 | 4 | 11.8488 | 49.0547 | 24.5274 | 20 | 20 | 4.5274 | 317.759
380 | 6.3333 | 2.0648 | 10.6073 | 2 | 10.4 | 48.9353 | 0 | -0.20725 | 169.2054 | -0.0029529 | -0.62176 | 8.4603 | -0.0088587 | 7.8297 |  | 11.8297 | 4 | 11.8297 | 48.9353 | 24.4677 | 20 | 20 | 4.4677 | 322.2266
381 | 6.35 | 2.0657 | 10.6102 | 2 | 10.4 | 48.8158 | 0 | -0.21017 | 168.9952 | -0.0029139 | -0.6305 | 8.4498 | -0.0087418 | 7.8105 |  | 11.8105 | 4 | 11.8105 | 48.8158 | 24.4079 | 20 | 20 | 4.4079 | 326.6345
382 | 6.3667 | 2.0666 | 10.613 | 2 | 10.4 | 48.696 | 0 | -0.21304 | 168.7821 | -0.0028749 | -0.63912 | 8.4391 | -0.0086248 | 7.7914 |  | 11.7914 | 4 | 11.7914 | 48.696 | 24.348 | 20 | 20 | 4.348 | 330.9825
383 | 6.3833 | 2.0675 | 10.6159 | 2 | 10.4 | 48.5761 | 0 | -0.21588 | 168.5663 | -0.0028359 | -0.64763 | 8.4283 | -0.0085077 | 7.7722 |  | 11.7722 | 4 | 11.7722 | 48.5761 | 24.2881 | 20 | 20 | 4.2881 | 335.2706
384 | 6.4 | 2.0683 | 10.6187 | 2 | 10.4 | 48.4561 | 0 | -0.21867 | 168.3476 | -0.0027968 | -0.65602 | 8.4174 | -0.0083904 | 7.753 |  | 11.753 | 4 | 11.753 | 48.4561 | 24.228 | 20 | 20 | 4.228 | 339.4986
385 | 6.4167 | 2.0692 | 10.6214 | 2 | 10.4 | 48.3359 | 0 | -0.22143 | 168.1262 | -0.0027576 | -0.66429 | 8.4063 | -0.0082729 | 7.7337 |  | 11.7337 | 4 | 11.7337 | 48.3359 | 24.1679 | 20 | 20 | 4.1679 | 343.6666
386 | 6.4333 | 2.07 | 10.6241 | 2 | 10.4 | 48.2156 | 0 | -0.22415 | 167.902 | -0.0027185 | -0.67245 | 8.3951 | -0.0081554 | 7.7145 |  | 11.7145 | 4 | 11.7145 | 48.2156 | 24.1078 | 20 | 20 | 4.1078 | 347.7744
387 | 6.45 | 2.0709 | 10.6268 | 2 | 10.4 | 48.0952 | 0 | -0.22683 | 167.6752 | -0.0026792 | -0.68049 | 8.3838 | -0.0080377 | 7.6952 |  | 11.6952 | 4 | 11.6952 | 48.0952 | 24.0476 | 20 | 20 | 4.0476 | 351.822
388 | 6.4667 | 2.0717 | 10.6295 | 2 | 10.4 | 47.9748 | 0 | -0.22947 | 167.4457 | -0.00264 | -0.68841 | 8.3723 | -0.0079199 | 7.676 |  | 11.676 | 4 | 11.676 | 47.9748 | 23.9874 | 20 | 20 | 3.9874 | 355.8093
389 | 6.4833 | 2.0725 | 10.6321 | 2 | 10.4 | 47.8542 | 0 | -0.23207 | 167.2137 | -0.0026007 | -0.69621 | 8.3607 | -0.0078021 | 7.6567 |  | 11.6567 | 4 | 11.6567 | 47.8542 | 23.9271 | 20 | 20 | 3.9271 | 359.7364
390 | 6.5 | 2.0733 | 10.6346 | 2 | 10.4 | 47.7336 | 0 | -0.23463 | 166.979 | -0.0025614 | -0.70389 | 8.349 | -0.0076841 | 7.6374 |  | 11.6374 | 4 | 11.6374 | 47.7336 | 23.8668 | 20 | 20 | 3.8668 | 363.6032
391 | 6.5167 | 2.0741 | 10.6372 | 2 | 10.4 | 47.6129 | 0 | -0.23715 | 166.7419 | -0.002522 | -0.71146 | 8.3371 | -0.0075661 | 7.6181 |  | 11.6181 | 4 | 11.6181 | 47.6129 | 23.8065 | 20 | 20 | 3.8065 | 367.4097
392 | 6.5333 | 2.0749 | 10.6396 | 2 | 10.4 | 47.4922 | 0 | -0.23964 | 166.5022 | -0.0024827 | -0.71891 | 8.3251 | -0.0074481 | 7.5988 |  | 11.5988 | 4 | 11.5988 | 47.4922 | 23.7461 | 20 | 20 | 3.7461 | 371.1558
393 | 6.55 | 2.0756 | 10.6421 | 2 | 10.4 | 47.3715 | 0 | -0.24208 | 166.2602 | -0.0024433 | -0.72624 | 8.313 | -0.00733 | 7.5794 |  | 11.5794 | 4 | 11.5794 | 47.3715 | 23.6858 | 20 | 20 | 3.6858 | 374.8416
394 | 6.5667 | 2.0764 | 10.6445 | 2 | 10.4 | 47.2508 | 0 | -0.24448 | 166.0157 | -0.002404 | -0.73345 | 8.3008 | -0.0072119 | 7.5601 |  | 11.5601 | 4 | 11.5601 | 47.2508 | 23.6254 | 20 | 20 | 3.6254 | 378.467
395 | 6.5833 | 2.0771 | 10.6468 | 2 | 10.4 | 47.13 | 0 | -0.24685 | 165.7688 | -0.0023646 | -0.74054 | 8.2884 | -0.0070937 | 7.5408 |  | 11.5408 | 4 | 11.5408 | 47.13 | 23.565 | 20 | 20 | 3.565 | 382.032
396 | 6.6 | 2.0779 | 10.6492 | 2 | 10.4 | 47.0093 | 0 | -0.24917 | 165.5197 | -0.0023252 | -0.74752 | 8.276 | -0.0069756 | 7.5215 |  | 11.5215 | 4 | 11.5215 | 47.0093 | 23.5047 | 20 | 20 | 3.5047 | 385.5366
397 | 6.6167 | 2.0786 | 10.6515 | 2 | 10.4 | 46.8886 | 0 | -0.25146 | 165.2682 | -0.0022858 | -0.75437 | 8.2634 | -0.0068575 | 7.5022 |  | 11.5022 | 4 | 11.5022 | 46.8886 | 23.4443 | 20 | 20 | 3.4443 | 388.9809
398 | 6.6333 | 2.0793 | 10.6537 | 2 | 10.4 | 46.7679 | 0 | -0.2537 | 165.0145 | -0.0022465 | -0.76111 | 8.2507 | -0.0067394 | 7.4829 |  | 11.4829 | 4 | 11.4829 | 46.7679 | 23.384 | 20 | 20 | 3.384 | 392.3649
399 | 6.65 | 2.08 | 10.6559 | 2 | 10.4 | 46.6473 | 0 | -0.25591 | 164.7586 | -0.0022071 | -0.76774 | 8.2379 | -0.0066214 | 7.4636 |  | 11.4636 | 4 | 11.4636 | 46.6473 | 23.3237 | 20 | 20 | 3.3237 | 395.6886
400 | 6.6667 | 2.0806 | 10.6581 | 2 | 10.4 | 46.5268 | 0 | -0.25808 | 164.5005 | -0.0021678 | -0.77424 | 8.225 | -0.0065034 | 7.4443 |  | 11.4443 | 4 | 11.4443 | 46.5268 | 23.2634 | 20 | 20 | 3.2634 | 398.952
401 | 6.6833 | 2.0813 | 10.6602 | 2 | 10.4 | 46.4063 | 0 | -0.26021 | 164.2403 | -0.0021285 | -0.78062 | 8.212 | -0.0063854 | 7.425 |  | 11.425 | 4 | 11.425 | 46.4063 | 23.2031 | 20 | 20 | 3.2031 | 402.1551
402 | 6.7 | 2.082 | 10.6623 | 2 | 10.4 | 46.2859 | 0 | -0.2623 | 163.978 | -0.0020892 | -0.78689 | 8.1989 | -0.0062675 | 7.4057 |  | 11.4057 | 4 | 11.4057 | 46.2859 | 23.1429 | 20 | 20 | 3.1429 | 405.298
403 | 6.7167 | 2.0826 | 10.6643 | 2 | 10.4 | 46.1656 | 0 | -0.26435 | 163.7136 | -0.0020499 | -0.79304 | 8.1857 | -0.0061497 | 7.3865 |  | 11.3865 | 4 | 11.3865 | 46.1656 | 23.0828 | 20 | 20 | 3.0828 | 408.3808
404 | 6.7333 | 2.0832 | 10.6664 | 2 | 10.4 | 46.0454 | 0 | -0.26636 | 163.4473 | -0.0020107 | -0.79907 | 8.1724 | -0.006032 | 7.3673 |  | 11.3673 | 4 | 11.3673 | 46.0454 | 23.0227 | 20 | 20 | 3.0227 | 411.4035
405 | 6.75 | 2.0839 | 10.6683 | 2 | 10.4 | 45.9253 | 0 | -0.26833 | 163.179 | -0.0019715 | -0.80499 | 8.1589 | -0.0059144 | 7.348 |  | 11.348 | 4 | 11.348 | 45.9253 | 22.9626 | 20 | 20 | 2.9626 | 414.3661
406 | 6.7667 | 2.0845 | 10.6703 | 2 | 10.4 | 45.8053 | 0 | -0.27026 | 162.9087 | -0.0019323 | -0.81079 | 8.1454 | -0.005797 | 7.3289 |  | 11.3289 | 4 | 11.3289 | 45.8053 | 22.9027 | 20 | 20 | 2.9027 | 417.2688
407 | 6.7833 | 2.085 | 10.6722 | 2 | 10.4 | 45.6855 | 0 | -0.27215 | 162.6365 | -0.0018932 | -0.81646 | 8.1318 | -0.0056796 | 7.3097 |  | 11.3097 | 4 | 11.3097 | 45.6855 | 22.8428 | 20 | 20 | 2.8428 | 420.1116
408 | 6.8 | 2.0856 | 10.674 | 2 | 10.4 | 45.5659 | 0 | -0.27401 | 162.3625 | -0.0018541 | -0.82203 | 8.1181 | -0.0055624 | 7.2905 |  | 11.2905 | 4 | 11.2905 | 45.5659 | 22.7829 | 20 | 20 | 2.7829 | 422.8945
409 | 6.8167 | 2.0862 | 10.6758 | 2 | 10.4 | 45.4464 | 0 | -0.27582 | 162.0867 | -0.0018151 | -0.82747 | 8.1043 | -0.0054453 | 7.2714 |  | 11.2714 | 4 | 11.2714 | 45.4464 | 22.7232 | 20 | 20 | 2.7232 | 425.6177
410 | 6.8333 | 2.0868 | 10.6776 | 2 | 10.4 | 45.327 | 0 | -0.2776 | 161.8091 | -0.0017761 | -0.8328 | 8.0905 | -0.0053284 | 7.2523 |  | 11.2523 | 4 | 11.2523 | 45.327 | 22.6635 | 20 | 20 | 2.6635 | 428.2812
411 | 6.85 | 2.0873 | 10.6793 | 2 | 10.4 | 45.2079 | 0 | -0.27934 | 161.5298 | -0.0017372 | -0.83801 | 8.0765 | -0.0052117 | 7.2333 |  | 11.2333 | 4 | 11.2333 | 45.2079 | 22.604 | 20 | 20 | 2.604 | 430.8851
412 | 6.8667 | 2.0878 | 10.681 | 2 | 10.4 | 45.089 | 0 | -0.28104 | 161.2487 | -0.0016984 | -0.84311 | 8.0624 | -0.0050951 | 7.2142 |  | 11.2142 | 4 | 11.2142 | 45.089 | 22.5445 | 20 | 20 | 2.5445 | 433.4296
413 | 6.8833 | 2.0883 | 10.6827 | 2 | 10.4 | 44.9702 | 0 | -0.2827 | 160.966 | -0.0016596 | -0.84809 | 8.0483 | -0.0049788 | 7.1952 |  | 11.1952 | 4 | 11.1952 | 44.9702 | 22.4851 | 20 | 20 | 2.4851 | 435.9147
414 | 6.9 | 2.0888 | 10.6843 | 2 | 10.4 | 44.8517 | 0 | -0.28432 | 160.6817 | -0.0016209 | -0.85295 | 8.0341 | -0.0048626 | 7.1763 |  | 11.1763 | 4 | 11.1763 | 44.8517 | 22.4259 | 20 | 20 | 2.4259 | 438.3406
415 | 6.9167 | 2.0893 | 10.6859 | 2 | 10.4 | 44.7334 | 0 | -0.2859 | 160.3958 | -0.0015822 | -0.8577 | 8.0198 | -0.0047466 | 7.1573 |  | 11.1573 | 4 | 11.1573 | 44.7334 | 22.3667 | 20 | 20 | 2.3667 | 440.7073
416 | 6.9333 | 2.0898 | 10.6874 | 2 | 10.4 | 44.6154 | 0 | -0.28744 | 160.1084 | -0.0015436 | -0.86233 | 8.0054 | -0.0046309 | 7.1385 |  | 11.1385 | 4 | 11.1385 | 44.6154 | 22.3077 | 20 | 20 | 2.3077 | 443.015
417 | 6.95 | 2.0903 | 10.6889 | 2 | 10.4 | 44.4976 | 0 | -0.28895 | 159.8194 | -0.0015051 | -0.86684 | 7.991 | -0.0045154 | 7.1196 |  | 11.1196 | 4 | 11.1196 | 44.4976 | 22.2488 | 20 | 20 | 2.2488 | 445.2638
418 | 6.9667 | 2.0908 | 10.6904 | 2 | 10.4 | 44.3801 | 0 | -0.29041 | 159.529 | -0.0014667 | -0.87124 | 7.9765 | -0.0044002 | 7.1008 |  | 11.1008 | 4 | 11.1008 | 44.3801 | 22.19 | 20 | 20 | 2.19 | 447.4538
419 | 6.9833 | 2.0912 | 10.6918 | 2 | 10.4 | 44.2628 | 0 | -0.29184 | 159.2372 | -0.0014284 | -0.87553 | 7.9619 | -0.0042852 | 7.082 |  | 11.082 | 4 | 11.082 | 44.2628 | 22.1314 | 20 | 20 | 2.1314 | 449.5852
420 | 7 | 2.0916 | 10.6932 | 2 | 10.4 | 44.1458 | 0 | -0.29323 | 158.9439 | -0.0013902 | -0.8797 | 7.9472 | -0.0041705 | 7.0633 |  | 11.0633 | 4 | 11.0633 | 44.1458 | 22.0729 | 20 | 20 | 2.0729 | 451.6581
421 | 7.0167 | 2.0921 | 10.6946 | 2 | 10.4 | 44.0291 | 0 | -0.29458 | 158.6494 | -0.001352 | -0.88375 | 7.9325 | -0.004056 | 7.0447 |  | 11.0447 | 4 | 11.0447 | 44.0291 | 22.0146 | 20 | 20 | 2.0146 | 453.6727
422 | 7.0333 | 2.0925 | 10.6959 | 2 | 10.4 | 43.9127 | 0 | -0.2959 | 158.3535 | -0.001314 | -0.8877 | 7.9177 | -0.0039419 | 7.026 |  | 11.026 | 4 | 11.026 | 43.9127 | 21.9564 | 20 | 20 | 1.9564 | 455.629
423 | 7.05 | 2.0929 | 10.6972 | 2 | 10.4 | 43.7966 | 0 | -0.29717 | 158.0563 | -0.001276 | -0.89152 | 7.9028 | -0.003828 | 7.0075 |  | 11.0075 | 4 | 11.0075 | 43.7966 | 21.8983 | 20 | 20 | 1.8983 | 457.5274
424 | 7.0667 | 2.0933 | 10.6984 | 2 | 10.4 | 43.6809 | 0 | -0.29841 | 157.7579 | -0.0012381 | -0.89524 | 7.8879 | -0.0037144 | 6.9889 |  | 10.9889 | 4 | 10.9889 | 43.6809 | 21.8404 | 20 | 20 | 1.8404 | 459.3678
425 | 7.0833 | 2.0936 | 10.6996 | 2 | 10.4 | 43.5655 | 0 | -0.29961 | 157.4583 | -0.0012004 | -0.89884 | 7.8729 | -0.0036012 | 6.9705 |  | 10.9705 | 4 | 10.9705 | 43.5655 | 21.7827 | 20 | 20 | 1.7827 | 461.1505
426 | 7.1 | 2.094 | 10.7008 | 2 | 10.4 | 43.4504 | 0 | -0.30078 | 157.1575 | -0.0011627 | -0.90233 | 7.8579 | -0.0034882 | 6.9521 |  | 10.9521 | 4 | 10.9521 | 43.4504 | 21.7252 | 20 | 20 | 1.7252 | 462.8757
427 | 7.1167 | 2.0943 | 10.7019 | 2 | 10.4 | 43.3356 | 0 | -0.3019 | 156.8556 | -0.0011252 | -0.9057 | 7.8428 | -0.0033756 | 6.9337 |  | 10.9337 | 4 | 10.9337 | 43.3356 | 21.6678 | 20 | 20 | 1.6678 | 464.5435
428 | 7.1333 | 2.0947 | 10.703 | 2 | 10.4 | 43.2212 | 0 | -0.30299 | 156.5526 | -0.0010878 | -0.90897 | 7.8276 | -0.0032634 | 6.9154 |  | 10.9154 | 4 | 10.9154 | 43.2212 | 21.6106 | 20 | 20 | 1.6106 | 466.1541
429 | 7.15 | 2.095 | 10.704 | 2 | 10.4 | 43.1072 | 0 | -0.30404 | 156.2486 | -0.0010505 | -0.91212 | 7.8124 | -0.0031515 | 6.8972 |  | 10.8972 | 4 | 10.8972 | 43.1072 | 21.5536 | 20 | 20 | 1.5536 | 467.7078
430 | 7.1667 | 2.0953 | 10.7051 | 2 | 10.4 | 42.9936 | 0 | -0.30505 | 155.9435 | -0.0010133 | -0.91516 | 7.7972 | -0.0030399 | 6.879 |  | 10.879 | 4 | 10.879 | 42.9936 | 21.4968 | 20 | 20 | 1.4968 | 469.2046
431 | 7.1833 | 2.0956 | 10.706 | 2 | 10.4 | 42.8804 | 0 | -0.30603 | 155.6375 | -0.00097626 | -0.91809 | 7.7819 | -0.0029288 | 6.8609 |  | 10.8609 | 4 | 10.8609 | 42.8804 | 21.4402 | 20 | 20 | 1.4402 | 470.6447
432 | 7.2 | 2.0959 | 10.707 | 2 | 10.4 | 42.7675 | 0 | -0.30697 | 155.3305 | -0.00093933 | -0.9209 | 7.7665 | -0.002818 | 6.8428 |  | 10.8428 | 4 | 10.8428 | 42.7675 | 21.3838 | 20 | 20 | 1.3838 | 472.0285
433 | 7.2167 | 2.0962 | 10.7079 | 2 | 10.4 | 42.6551 | 0 | -0.30787 | 155.0226 | -0.00090253 | -0.92361 | 7.7511 | -0.0027076 | 6.8248 |  | 10.8248 | 4 | 10.8248 | 42.6551 | 21.3275 | 20 | 20 | 1.3275 | 473.356
434 | 7.2333 | 2.0965 | 10.7087 | 2 | 10.4 | 42.543 | 0 | -0.30874 | 154.7139 | -0.00086586 | -0.92621 | 7.7357 | -0.0025976 | 6.8069 |  | 10.8069 | 4 | 10.8069 | 42.543 | 21.2715 | 20 | 20 | 1.2715 | 474.6276
435 | 7.25 | 2.0967 | 10.7096 | 2 | 10.4 | 42.4314 | 0 | -0.30957 | 154.4043 | -0.00082932 | -0.9287 | 7.7202 | -0.002488 | 6.789 |  | 10.789 | 4 | 10.789 | 42.4314 | 21.2157 | 20 | 20 | 1.2157 | 475.8433
436 | 7.2667 | 2.097 | 10.7104 | 2 | 10.4 | 42.3203 | 0 | -0.31036 | 154.094 | -0.00079293 | -0.93108 | 7.7047 | -0.0023788 | 6.7712 |  | 10.7712 | 4 | 10.7712 | 42.3203 | 21.1601 | 20 | 20 | 1.1601 | 477.0034
437 | 7.2833 | 2.0972 | 10.7111 | 2 | 10.4 | 42.2095 | 0 | -0.31112 | 153.7829 | -0.00075667 | -0.93335 | 7.6891 | -0.00227 | 6.7535 |  | 10.7535 | 4 | 10.7535 | 42.2095 | 21.1048 | 20 | 20 | 1.1048 | 478.1082
438 | 7.3 | 2.0974 | 10.7118 | 2 | 10.4 | 42.0993 | 0 | -0.31184 | 153.471 | -0.00072056 | -0.93551 | 7.6736 | -0.0021617 | 6.7359 |  | 10.7359 | 4 | 10.7359 | 42.0993 | 21.0496 | 20 | 20 | 1.0496 | 479.1578
439 | 7.3167 | 2.0977 | 10.7125 | 2 | 10.4 | 41.9894 | 0 | -0.31252 | 153.1585 | -0.0006846 | -0.93756 | 7.6579 | -0.0020538 | 6.7183 |  | 10.7183 | 4 | 10.7183 | 41.9894 | 20.9947 | 20 | 20 | 0.99472 | 480.1525
440 | 7.3333 | 2.0979 | 10.7132 | 2 | 10.4 | 41.8801 | 0 | -0.31317 | 152.8453 | -0.00064878 | -0.93951 | 7.6423 | -0.0019463 | 6.7008 |  | 10.7008 | 4 | 10.7008 | 41.8801 | 20.94 | 20 | 20 | 0.94004 | 481.0926
441 | 7.35 | 2.0981 | 10.7138 | 2 | 10.4 | 41.7712 | 0 | -0.31378 | 152.5315 | -0.00061312 | -0.94135 | 7.6266 | -0.0018394 | 6.6834 |  | 10.6834 | 4 | 10.6834 | 41.7712 | 20.8856 | 20 | 20 | 0.88559 | 481.9782
442 | 7.3667 | 2.0982 | 10.7144 | 2 | 10.4 | 41.6628 | 0 | -0.31436 | 152.2172 | -0.00057761 | -0.94308 | 7.6109 | -0.0017328 | 6.666 |  | 10.666 | 4 | 10.666 | 41.6628 | 20.8314 | 20 | 20 | 0.83139 | 482.8095
443 | 7.3833 | 2.0984 | 10.7149 | 2 | 10.4 | 41.5549 | 0 | -0.3149 | 151.9023 | -0.00054226 | -0.94471 | 7.5951 | -0.0016268 | 6.6488 |  | 10.6488 | 4 | 10.6488 | 41.5549 | 20.7774 | 20 | 20 | 0.77744 | 483.587
444 | 7.4 | 2.0986 | 10.7154 | 2 | 10.4 | 41.4475 | 0 | -0.31541 | 151.5869 | -0.00050707 | -0.94623 | 7.5793 | -0.0015212 | 6.6316 |  | 10.6316 | 4 | 10.6316 | 41.4475 | 20.7237 | 20 | 20 | 0.72373 | 484.3107
445 | 7.4167 | 2.0987 | 10.7159 | 2 | 10.4 | 41.3406 | 0 | -0.31588 | 151.271 | -0.00047204 | -0.94764 | 7.5635 | -0.0014161 | 6.6145 |  | 10.6145 | 4 | 10.6145 | 41.3406 | 20.6703 | 20 | 20 | 0.67028 | 484.981
446 | 7.4333 | 2.0988 | 10.7163 | 2 | 10.4 | 41.2342 | 0 | -0.31632 | 150.9547 | -0.00043717 | -0.94896 | 7.5477 | -0.0013115 | 6.5975 |  | 10.5975 | 4 | 10.5975 | 41.2342 | 20.6171 | 20 | 20 | 0.61708 | 485.5981
447 | 7.45 | 2.099 | 10.7167 | 2 | 10.4 | 41.1283 | 0 | -0.31672 | 150.638 | -0.00040248 | -0.95016 | 7.5319 | -0.0012074 | 6.5805 |  | 10.5805 | 4 | 10.5805 | 41.1283 | 20.5641 | 20 | 20 | 0.56414 | 486.1622
448 | 7.4667 | 2.0991 | 10.7171 | 2 | 10.4 | 41.0229 | 0 | -0.31709 | 150.3209 | -0.00036795 | -0.95127 | 7.516 | -0.0011039 | 6.5637 |  | 10.5637 | 4 | 10.5637 | 41.0229 | 20.5115 | 20 | 20 | 0.51147 | 486.6737
449 | 7.4833 | 2.0992 | 10.7174 | 2 | 10.4 | 40.9181 | 0 | -0.31742 | 150.0034 | -0.0003336 | -0.95227 | 7.5002 | -0.0010008 | 6.5469 |  | 10.5469 | 4 | 10.5469 | 40.9181 | 20.4591 | 20 | 20 | 0.45907 | 487.1328
450 | 7.5 | 2.0993 | 10.7177 | 2 | 10.4 | 40.8139 | 0 | -0.31772 | 149.6857 | -0.00029942 | -0.95317 | 7.4843 | -0.00089826 | 6.5302 |  | 10.5302 | 4 | 10.5302 | 40.8139 | 20.4069 | 20 | 20 | 0.40694 | 487.5397
451 | 7.5167 | 2.0994 | 10.718 | 2 | 10.4 | 40.7102 | 0 | -0.31799 | 149.3677 | -0.00026542 | -0.95396 | 7.4684 | -0.00079626 | 6.5136 |  | 10.5136 | 4 | 10.5136 | 40.7102 | 20.3551 | 20 | 20 | 0.35509 | 487.8948
452 | 7.5333 | 2.0994 | 10.7182 | 2 | 10.4 | 40.607 | 0 | -0.31822 | 149.0495 | -0.0002316 | -0.95466 | 7.4525 | -0.00069479 | 6.4971 |  | 10.4971 | 4 | 10.4971 | 40.607 | 20.3035 | 20 | 20 | 0.30351 | 488.1983
453 | 7.55 | 2.0995 | 10.7184 | 2 | 10.4 | 40.5044 | 0 | -0.31842 | 148.7311 | -0.00019796 | -0.95525 | 7.4366 | -0.00059387 | 6.4807 |  | 10.4807 | 4 | 10.4807 | 40.5044 | 20.2522 | 20 | 20 | 0.25222 | 488.4505
454 | 7.5667 | 2.0996 | 10.7186 | 2 | 10.4 | 40.4024 | 0 | -0.31858 | 148.4125 | -0.0001645 | -0.95575 | 7.4206 | -0.00049351 | 6.4644 |  | 10.4644 | 4 | 10.4644 | 40.4024 | 20.2012 | 20 | 20 | 0.20121 | 488.6517
455 | 7.5833 | 2.0996 | 10.7187 | 2 | 10.4 | 40.301 | 0 | -0.31871 | 148.0938 | -0.00013123 | -0.95614 | 7.4047 | -0.0003937 | 6.4482 |  | 10.4482 | 4 | 10.4482 | 40.301 | 20.1505 | 20 | 20 | 0.15049 | 488.8022
456 | 7.6 | 2.0996 | 10.7188 | 2 | 10.4 | 40.2001 | 0 | -0.31881 | 147.775 | -9.8155e-05 | -0.95643 | 7.3887 | -0.00029447 | 6.432 |  | 10.432 | 4 | 10.432 | 40.2001 | 20.1001 | 20 | 20 | 0.10007 | 488.9023
457 | 7.6167 | 2.0996 | 10.7189 | 2 | 10.4 | 40.0999 | 0 | -0.31888 | 147.4561 | -6.5267e-05 | -0.95663 | 7.3728 | -0.0001958 | 6.416 |  | 10.416 | 4 | 10.416 | 40.0999 | 20.0499 | 20 | 20 | 0.049939 | 488.9522
458 | 7.6333 | 2.0997 | 10.7189 | 2 | 10.4 | 40.0002 | 0 | -0.31891 | 147.1372 | -3.2572e-05 | -0.95673 | 7.3569 | -9.7716e-05 | 6.4 |  | 10.4 | 4 | 10.4 | 40.0002 | 20.0001 | 20 | 20 | 0.0001111 | 488.9523
459 | 7.65 | 2.0997 | 10.7189 | 2 | 10.4 | 39.9012 | 0 | -0.31891 | 146.8183 | -7.2464e-08 | -0.95673 | 7.3409 | -2.1739e-07 | 6.3842 |  | 10.3842 | 4 | 10.3842 | 39.9012 | 19.9506 | 20 | 20 | -0.049414 | 488.9029
460 | 7.6667 | 2.0996 | 10.7189 | 2 | 10.4 | 39.8027 | 0 | -0.31888 | 146.4994 | 3.223e-05 | -0.95663 | 7.325 | 9.6689e-05 | 6.3684 |  | 10.3684 | 4 | 10.3684 | 39.8027 | 19.9014 | 20 | 20 | -0.098634 | 488.8043
461 | 7.6833 | 2.0996 | 10.7188 | 2 | 10.4 | 39.7049 | 0 | -0.31881 | 146.1806 | 6.4332e-05 | -0.95644 | 7.309 | 0.000193 | 6.3528 |  | 10.3528 | 4 | 10.3528 | 39.7049 | 19.8525 | 20 | 20 | -0.14754 | 488.6567
462 | 7.7 | 2.0996 | 10.7187 | 2 | 10.4 | 39.6077 | 0 | -0.31872 | 145.8619 | 9.6233e-05 | -0.95615 | 7.2931 | 0.0002887 | 6.3372 |  | 10.3372 | 4 | 10.3372 | 39.6077 | 19.8039 | 20 | 20 | -0.19614 | 488.4606
463 | 7.7167 | 2.0996 | 10.7186 | 2 | 10.4 | 39.5111 | 0 | -0.31859 | 145.5433 | 0.00012793 | -0.95576 | 7.2772 | 0.00038379 | 6.3218 |  | 10.3218 | 4 | 10.3218 | 39.5111 | 19.7556 | 20 | 20 | -0.24443 | 488.2162
464 | 7.7333 | 2.0995 | 10.7184 | 2 | 10.4 | 39.4152 | 0 | -0.31843 | 145.2249 | 0.00015942 | -0.95529 | 7.2612 | 0.00047826 | 6.3064 |  | 10.3064 | 4 | 10.3064 | 39.4152 | 19.7076 | 20 | 20 | -0.29239 | 487.9238
465 | 7.75 | 2.0994 | 10.7182 | 2 | 10.4 | 39.3199 | 0 | -0.31824 | 144.9066 | 0.00019071 | -0.95471 | 7.2453 | 0.00057212 | 6.2912 |  | 10.2912 | 4 | 10.2912 | 39.3199 | 19.66 | 20 | 20 | -0.34003 | 487.5837
466 | 7.7667 | 2.0994 | 10.718 | 2 | 10.4 | 39.2253 | 0 | -0.31802 | 144.5886 | 0.00022178 | -0.95405 | 7.2294 | 0.00066534 | 6.276 |  | 10.276 | 4 | 10.276 | 39.2253 | 19.6126 | 20 | 20 | -0.38735 | 487.1964
467 | 7.7833 | 2.0993 | 10.7178 | 2 | 10.4 | 39.1313 | 0 | -0.31776 | 144.2709 | 0.00025264 | -0.95329 | 7.2135 | 0.00075793 | 6.261 |  | 10.261 | 4 | 10.261 | 39.1313 | 19.5657 | 20 | 20 | -0.43435 | 486.762
468 | 7.8 | 2.0992 | 10.7175 | 2 | 10.4 | 39.038 | 0 | -0.31748 | 143.9534 | 0.00028329 | -0.95244 | 7.1977 | 0.00084988 | 6.2461 |  | 10.2461 | 4 | 10.2461 | 39.038 | 19.519 | 20 | 20 | -0.48101 | 486.281
469 | 7.8167 | 2.0991 | 10.7172 | 2 | 10.4 | 38.9453 | 0 | -0.31717 | 143.6362 | 0.00031373 | -0.9515 | 7.1818 | 0.00094118 | 6.2313 |  | 10.2313 | 4 | 10.2313 | 38.9453 | 19.4727 | 20 | 20 | -0.52734 | 485.7537
470 | 7.8333 | 2.099 | 10.7168 | 2 | 10.4 | 38.8533 | 0 | -0.31682 | 143.3194 | 0.00034395 | -0.95047 | 7.166 | 0.0010318 | 6.2165 |  | 10.2165 | 4 | 10.2165 | 38.8533 | 19.4267 | 20 | 20 | -0.57334 | 485.1804
471 | 7.85 | 2.0989 | 10.7164 | 2 | 10.4 | 38.762 | 0 | -0.31645 | 143.0029 | 0.00037395 | -0.94935 | 7.1501 | 0.0011218 | 6.2019 |  | 10.2019 | 4 | 10.2019 | 38.762 | 19.381 | 20 | 20 | -0.61899 | 484.5614
472 | 7.8667 | 2.0988 | 10.716 | 2 | 10.4 | 38.6714 | 0 | -0.31605 | 142.6869 | 0.00040373 | -0.94814 | 7.1343 | 0.0012112 | 6.1874 |  | 10.1874 | 4 | 10.1874 | 38.6714 | 19.3357 | 20 | 20 | -0.66431 | 483.8971
473 | 7.8833 | 2.0986 | 10.7156 | 2 | 10.4 | 38.5814 | 0 | -0.31561 | 142.3713 | 0.00043328 | -0.94684 | 7.1186 | 0.0012999 | 6.173 |  | 10.173 | 4 | 10.173 | 38.5814 | 19.2907 | 20 | 20 | -0.70929 | 483.1878
474 | 7.9 | 2.0985 | 10.7151 | 2 | 10.4 | 38.4922 | 0 | -0.31515 | 142.0561 | 0.00046262 | -0.94545 | 7.1028 | 0.0013879 | 6.1587 |  | 10.1587 | 4 | 10.1587 | 38.4922 | 19.2461 | 20 | 20 | -0.75392 | 482.4339
475 | 7.9167 | 2.0983 | 10.7147 | 2 | 10.4 | 38.4036 | 0 | -0.31466 | 141.7415 | 0.00049173 | -0.94397 | 7.0871 | 0.0014752 | 6.1446 |  | 10.1446 | 4 | 10.1446 | 38.4036 | 19.2018 | 20 | 20 | -0.7982 | 481.6357
476 | 7.9333 | 2.0982 | 10.7141 | 2 | 10.4 | 38.3157 | 0 | -0.31414 | 141.4273 | 0.00052061 | -0.94241 | 7.0714 | 0.0015618 | 6.1305 |  | 10.1305 | 4 | 10.1305 | 38.3157 | 19.1579 | 20 | 20 | -0.84213 | 480.7935
477 | 7.95 | 2.098 | 10.7136 | 2 | 10.4 | 38.2286 | 0 | -0.31359 | 141.1137 | 0.00054926 | -0.94076 | 7.0557 | 0.0016478 | 6.1166 |  | 10.1166 | 4 | 10.1166 | 38.2286 | 19.1143 | 20 | 20 | -0.88571 | 479.9078
478 | 7.9667 | 2.0978 | 10.713 | 2 | 10.4 | 38.1421 | 0 | -0.31301 | 140.8007 | 0.00057769 | -0.93903 | 7.04 | 0.0017331 | 6.1027 |  | 10.1027 | 4 | 10.1027 | 38.1421 | 19.0711 | 20 | 20 | -0.92894 | 478.9789
479 | 7.9833 | 2.0976 | 10.7124 | 2 | 10.4 | 38.0564 | 0 | -0.3124 | 140.4883 | 0.00060588 | -0.93721 | 7.0244 | 0.0018176 | 6.089 |  | 10.089 | 4 | 10.089 | 38.0564 | 19.0282 | 20 | 20 | -0.97181 | 478.0071
480 | 8 | 2.0974 | 10.7118 | 2 | 10.4 | 37.9714 | 0 | -0.31177 | 140.1766 | 0.00063384 | -0.93531 | 7.0088 | 0.0019015 | 6.0754 |  | 10.0754 | 4 | 10.0754 | 37.9714 | 18.9857 | 20 | 20 | -1.0143 | 476.9928
481 | 8.0167 | 2.0972 | 10.7111 | 2 | 10.4 | 37.8871 | 0 | -0.31111 | 139.8655 | 0.00066157 | -0.93333 | 6.9933 | 0.0019847 | 6.0619 |  | 10.0619 | 4 | 10.0619 | 37.8871 | 18.9435 | 20 | 20 | -1.0565 | 475.9363
482 | 8.0333 | 2.097 | 10.7104 | 2 | 10.4 | 37.8035 | 0 | -0.31042 | 139.555 | 0.00068906 | -0.93126 | 6.9778 | 0.0020672 | 6.0486 |  | 10.0486 | 4 | 10.0486 | 37.8035 | 18.9018 | 20 | 20 | -1.0982 | 474.838
483 | 8.05 | 2.0968 | 10.7097 | 2 | 10.4 | 37.7207 | 0 | -0.3097 | 139.2453 | 0.00071631 | -0.92911 | 6.9623 | 0.0021489 | 6.0353 |  | 10.0353 | 4 | 10.0353 | 37.7207 | 18.8603 | 20 | 20 | -1.1397 | 473.6984
484 | 8.0667 | 2.0965 | 10.709 | 2 | 10.4 | 37.6386 | 0 | -0.30896 | 138.9364 | 0.00074333 | -0.92688 | 6.9468 | 0.00223 | 6.0222 |  | 10.0222 | 4 | 10.0222 | 37.6386 | 18.8193 | 20 | 20 | -1.1807 | 472.5176
485 | 8.0833 | 2.0963 | 10.7082 | 2 | 10.4 | 37.5572 | 0 | -0.30819 | 138.6282 | 0.0007701 | -0.92457 | 6.9314 | 0.0023103 | 6.0091 |  | 10.0091 | 4 | 10.0091 | 37.5572 | 18.7786 | 20 | 20 | -1.2214 | 471.2962
486 | 8.1 | 2.0961 | 10.7074 | 2 | 10.4 | 37.4766 | 0 | -0.30739 | 138.3208 | 0.00079664 | -0.92218 | 6.916 | 0.0023899 | 5.9962 |  | 9.9962 | 4 | 9.9962 | 37.4766 | 18.7383 | 20 | 20 | -1.2617 | 470.0345
487 | 8.1167 | 2.0958 | 10.7066 | 2 | 10.4 | 37.3967 | 0 | -0.30657 | 138.0142 | 0.00082293 | -0.91971 | 6.9007 | 0.0024688 | 5.9835 |  | 9.9835 | 4 | 9.9835 | 37.3967 | 18.6983 | 20 | 20 | -1.3017 | 468.7329
488 | 8.1333 | 2.0955 | 10.7057 | 2 | 10.4 | 37.3175 | 0 | -0.30572 | 137.7085 | 0.00084898 | -0.91716 | 6.8854 | 0.0025469 | 5.9708 |  | 9.9708 | 4 | 9.9708 | 37.3175 | 18.6588 | 20 | 20 | -1.3412 | 467.3916
489 | 8.15 | 2.0953 | 10.7048 | 2 | 10.4 | 37.2392 | 0 | -0.30485 | 137.4036 | 0.00087479 | -0.91454 | 6.8702 | 0.0026244 | 5.9583 |  | 9.9583 | 4 | 9.9583 | 37.2392 | 18.6196 | 20 | 20 | -1.3804 | 466.0112
490 | 8.1667 | 2.095 | 10.7039 | 2 | 10.4 | 37.1615 | 0 | -0.30395 | 137.0997 | 0.00090035 | -0.91184 | 6.855 | 0.002701 | 5.9458 |  | 9.9458 | 4 | 9.9458 | 37.1615 | 18.5808 | 20 | 20 | -1.4192 | 464.592
491 | 8.1833 | 2.0947 | 10.703 | 2 | 10.4 | 37.0847 | 0 | -0.30302 | 136.7967 | 0.00092566 | -0.90906 | 6.8398 | 0.002777 | 5.9335 |  | 9.9335 | 4 | 9.9335 | 37.0847 | 18.5423 | 20 | 20 | -1.4577 | 463.1343
492 | 8.2 | 2.0944 | 10.7021 | 2 | 10.4 | 37.0086 | 0 | -0.30207 | 136.4946 | 0.00095073 | -0.90621 | 6.8247 | 0.0028522 | 5.9214 |  | 9.9214 | 4 | 9.9214 | 37.0086 | 18.5043 | 20 | 20 | -1.4957 | 461.6386
493 | 8.2167 | 2.0941 | 10.7011 | 2 | 10.4 | 36.9332 | 0 | -0.30109 | 136.1935 | 0.00097554 | -0.90328 | 6.8097 | 0.0029266 | 5.9093 |  | 9.9093 | 4 | 9.9093 | 36.9332 | 18.4666 | 20 | 20 | -1.5334 | 460.1052
494 | 8.2333 | 2.0938 | 10.7001 | 2 | 10.4 | 36.8587 | 0 | -0.30009 | 135.8934 | 0.0010001 | -0.90028 | 6.7947 | 0.0030003 | 5.8974 |  | 9.8974 | 4 | 9.8974 | 36.8587 | 18.4293 | 20 | 20 | -1.5707 | 458.5346
495 | 8.25 | 2.0935 | 10.6991 | 2 | 10.4 | 36.7849 | 0 | -0.29907 | 135.5944 | 0.0010244 | -0.89721 | 6.7797 | 0.0030733 | 5.8856 |  | 9.8856 | 4 | 9.8856 | 36.7849 | 18.3924 | 20 | 20 | -1.6076 | 456.927
496 | 8.2667 | 2.0931 | 10.698 | 2 | 10.4 | 36.7119 | 0 | -0.29802 | 135.2963 | 0.0010485 | -0.89406 | 6.7648 | 0.0031455 | 5.8739 |  | 9.8739 | 4 | 9.8739 | 36.7119 | 18.3559 | 20 | 20 | -1.6441 | 455.283
497 | 8.2833 | 2.0928 | 10.6969 | 2 | 10.4 | 36.6396 | 0 | -0.29695 | 134.9994 | 0.0010723 | -0.89085 | 6.75 | 0.0032169 | 5.8623 |  | 9.8623 | 4 | 9.8623 | 36.6396 | 18.3198 | 20 | 20 | -1.6802 | 453.6028
498 | 8.3 | 2.0925 | 10.6959 | 2 | 10.4 | 36.5682 | 0 | -0.29585 | 134.7035 | 0.0010959 | -0.88756 | 6.7352 | 0.0032876 | 5.8509 |  | 9.8509 | 4 | 9.8509 | 36.5682 | 18.2841 | 20 | 20 | -1.7159 | 451.8869
499 | 8.3167 | 2.0921 | 10.6947 | 2 | 10.4 | 36.4975 | 0 | -0.29473 | 134.4088 | 0.0011192 | -0.8842 | 6.7204 | 0.0033575 | 5.8396 |  | 9.8396 | 4 | 9.8396 | 36.4975 | 18.2487 | 20 | 20 | -1.7513 | 450.1356
500 | 8.3333 | 2.0917 | 10.6936 | 2 | 10.4 | 36.4276 | 0 | -0.29359 | 134.1152 | 0.0011422 | -0.88077 | 6.7058 | 0.0034267 | 5.8284 |  | 9.8284 | 4 | 9.8284 | 36.4276 | 18.2138 | 20 | 20 | -1.7862 | 448.3494
501 | 8.35 | 2.0914 | 10.6924 | 2 | 10.4 | 36.3585 | 0 | -0.29243 | 133.8228 | 0.001165 | -0.87728 | 6.6911 | 0.0034951 | 5.8174 |  | 9.8174 | 4 | 9.8174 | 36.3585 | 18.1792 | 20 | 20 | -1.8208 | 446.5286
502 | 8.3667 | 2.091 | 10.6912 | 2 | 10.4 | 36.2901 | 0 | -0.29124 | 133.5315 | 0.0011876 | -0.87372 | 6.6766 | 0.0035627 | 5.8064 |  | 9.8064 | 4 | 9.8064 | 36.2901 | 18.1451 | 20 | 20 | -1.8549 | 444.6737
503 | 8.3833 | 2.0906 | 10.69 | 2 | 10.4 | 36.2226 | 0 | -0.29003 | 133.2415 | 0.0012098 | -0.87009 | 6.6621 | 0.0036295 | 5.7956 |  | 9.7956 | 4 | 9.7956 | 36.2226 | 18.1113 | 20 | 20 | -1.8887 | 442.785
504 | 8.4 | 2.0902 | 10.6888 | 2 | 10.4 | 36.1559 | 0 | -0.2888 | 132.9527 | 0.0012319 | -0.86639 | 6.6476 | 0.0036956 | 5.7849 |  | 9.7849 | 4 | 9.7849 | 36.1559 | 18.0779 | 20 | 20 | -1.9221 | 440.8629
505 | 8.4167 | 2.0899 | 10.6875 | 2 | 10.4 | 36.0899 | 0 | -0.28754 | 132.6652 | 0.0012536 | -0.86263 | 6.6333 | 0.0037609 | 5.7744 |  | 9.7744 | 4 | 9.7744 | 36.0899 | 18.045 | 20 | 20 | -1.955 | 438.9079
506 | 8.4333 | 2.0895 | 10.6863 | 2 | 10.4 | 36.0248 | 0 | -0.28627 | 132.3789 | 0.0012751 | -0.85881 | 6.6189 | 0.0038254 | 5.764 |  | 9.764 | 4 | 9.764 | 36.0248 | 18.0124 | 20 | 20 | -1.9876 | 436.9203
507 | 8.45 | 2.0891 | 10.685 | 2 | 10.4 | 35.9604 | 0 | -0.28497 | 132.0939 | 0.0012964 | -0.85492 | 6.6047 | 0.0038891 | 5.7537 |  | 9.7537 | 4 | 9.7537 | 35.9604 | 17.9802 | 20 | 20 | -2.0198 | 434.9005
508 | 8.4667 | 2.0886 | 10.6837 | 2 | 10.4 | 35.8969 | 0 | -0.28365 | 131.8103 | 0.0013174 | -0.85096 | 6.5905 | 0.0039521 | 5.7435 |  | 9.7435 | 4 | 9.7435 | 35.8969 | 17.9484 | 20 | 20 | -2.0516 | 432.8489
509 | 8.4833 | 2.0882 | 10.6823 | 2 | 10.4 | 35.8341 | 0 | -0.28232 | 131.528 | 0.0013381 | -0.84695 | 6.5764 | 0.0040143 | 5.7335 |  | 9.7335 | 4 | 9.7335 | 35.8341 | 17.9171 | 20 | 20 | -2.0829 | 430.766
510 | 8.5 | 2.0878 | 10.681 | 2 | 10.4 | 35.7722 | 0 | -0.28096 | 131.247 | 0.0013585 | -0.84287 | 6.5623 | 0.0040756 | 5.7236 |  | 9.7236 | 4 | 9.7236 | 35.7722 | 17.8861 | 20 | 20 | -2.1139 | 428.6521
511 | 8.5167 | 2.0874 | 10.6796 | 2 | 10.4 | 35.7111 | 0 | -0.27958 | 130.9674 | 0.0013787 | -0.83874 | 6.5484 | 0.0041362 | 5.7138 |  | 9.7138 | 4 | 9.7138 | 35.7111 | 17.8555 | 20 | 20 | -2.1445 | 426.5076
512 | 8.5333 | 2.0869 | 10.6782 | 2 | 10.4 | 35.6507 | 0 | -0.27818 | 130.6892 | 0.0013987 | -0.83454 | 6.5345 | 0.0041961 | 5.7041 |  | 9.7041 | 4 | 9.7041 | 35.6507 | 17.8254 | 20 | 20 | -2.1746 | 424.333
513 | 8.55 | 2.0865 | 10.6768 | 2 | 10.4 | 35.5912 | 0 | -0.27676 | 130.4125 | 0.0014184 | -0.83029 | 6.5206 | 0.0042551 | 5.6946 |  | 9.6946 | 4 | 9.6946 | 35.5912 | 17.7956 | 20 | 20 | -2.2044 | 422.1286
514 | 8.5667 | 2.086 | 10.6753 | 2 | 10.4 | 35.5325 | 0 | -0.27532 | 130.1372 | 0.0014378 | -0.82597 | 6.5069 | 0.0043133 | 5.6852 |  | 9.6852 | 4 | 9.6852 | 35.5325 | 17.7662 | 20 | 20 | -2.2338 | 419.8948
515 | 8.5833 | 2.0856 | 10.6739 | 2 | 10.4 | 35.4746 | 0 | -0.27387 | 129.8633 | 0.0014569 | -0.8216 | 6.4932 | 0.0043708 | 5.6759 |  | 9.6759 | 4 | 9.6759 | 35.4746 | 17.7373 | 20 | 20 | -2.2627 | 417.6321
516 | 8.6 | 2.0851 | 10.6724 | 2 | 10.4 | 35.4175 | 0 | -0.27239 | 129.5909 | 0.0014758 | -0.81718 | 6.4795 | 0.0044274 | 5.6668 |  | 9.6668 | 4 | 9.6668 | 35.4175 | 17.7087 | 20 | 20 | -2.2913 | 415.3409
517 | 8.6167 | 2.0847 | 10.6709 | 2 | 10.4 | 35.3612 | 0 | -0.2709 | 129.32 | 0.0014944 | -0.81269 | 6.466 | 0.0044833 | 5.6578 |  | 9.6578 | 4 | 9.6578 | 35.3612 | 17.6806 | 20 | 20 | -2.3194 | 413.0214
518 | 8.6333 | 2.0842 | 10.6694 | 2 | 10.4 | 35.3057 | 0 | -0.26938 | 129.0506 | 0.0015128 | -0.80815 | 6.4525 | 0.0045384 | 5.6489 |  | 9.6489 | 4 | 9.6489 | 35.3057 | 17.6529 | 20 | 20 | -2.3471 | 410.6743
519 | 8.65 | 2.0837 | 10.6679 | 2 | 10.4 | 35.2511 | 0 | -0.26785 | 128.7828 | 0.0015309 | -0.80356 | 6.4391 | 0.0045926 | 5.6402 |  | 9.6402 | 4 | 9.6402 | 35.2511 | 17.6255 | 20 | 20 | -2.3745 | 408.2998
520 | 8.6667 | 2.0832 | 10.6663 | 2 | 10.4 | 35.1972 | 0 | -0.26631 | 128.5165 | 0.0015487 | -0.79892 | 6.4258 | 0.0046461 | 5.6316 |  | 9.6316 | 4 | 9.6316 | 35.1972 | 17.5986 | 20 | 20 | -2.4014 | 405.8984
521 | 8.6833 | 2.0827 | 10.6647 | 2 | 10.4 | 35.1442 | 0 | -0.26474 | 128.2517 | 0.0015663 | -0.79422 | 6.4126 | 0.0046988 | 5.6231 |  | 9.6231 | 4 | 9.6231 | 35.1442 | 17.5721 | 20 | 20 | -2.4279 | 403.4705
522 | 8.7 | 2.0822 | 10.6632 | 2 | 10.4 | 35.092 | 0 | -0.26316 | 127.9886 | 0.0015836 | -0.78947 | 6.3994 | 0.0047507 | 5.6147 |  | 9.6147 | 4 | 9.6147 | 35.092 | 17.546 | 20 | 20 | -2.454 | 401.0165
523 | 8.7167 | 2.0817 | 10.6616 | 2 | 10.4 | 35.0405 | 0 | -0.26155 | 127.727 | 0.0016006 | -0.78466 | 6.3864 | 0.0048018 | 5.6065 |  | 9.6065 | 4 | 9.6065 | 35.0405 | 17.5203 | 20 | 20 | -2.4797 | 398.5368
524 | 8.7333 | 2.0812 | 10.6599 | 2 | 10.4 | 34.99 | 0 | -0.25994 | 127.4671 | 0.0016173 | -0.77981 | 6.3734 | 0.004852 | 5.5984 |  | 9.5984 | 4 | 9.5984 | 34.99 | 17.495 | 20 | 20 | -2.505 | 396.0318
525 | 8.75 | 2.0807 | 10.6583 | 2 | 10.4 | 34.9402 | 0 | -0.2583 | 127.2088 | 0.0016338 | -0.77491 | 6.3604 | 0.0049015 | 5.5904 |  | 9.5904 | 4 | 9.5904 | 34.9402 | 17.4701 | 20 | 20 | -2.5299 | 393.5018
526 | 8.7667 | 2.0802 | 10.6567 | 2 | 10.4 | 34.8912 | 0 | -0.25665 | 126.9521 | 0.0016501 | -0.76996 | 6.3476 | 0.0049502 | 5.5826 |  | 9.5826 | 4 | 9.5826 | 34.8912 | 17.4456 | 20 | 20 | -2.5544 | 390.9475
527 | 8.7833 | 2.0797 | 10.655 | 2 | 10.4 | 34.8431 | 0 | -0.25499 | 126.6971 | 0.001666 | -0.76496 | 6.3349 | 0.0049981 | 5.5749 |  | 9.5749 | 4 | 9.5749 | 34.8431 | 17.4215 | 20 | 20 | -2.5785 | 388.369
528 | 8.8 | 2.0792 | 10.6533 | 2 | 10.4 | 34.7957 | 0 | -0.25331 | 126.4438 | 0.0016817 | -0.75992 | 6.3222 | 0.0050452 | 5.5673 |  | 9.5673 | 4 | 9.5673 | 34.7957 | 17.3979 | 20 | 20 | -2.6021 | 385.7669
529 | 8.8167 | 2.0786 | 10.6516 | 2 | 10.4 | 34.7492 | 0 | -0.25161 | 126.1922 | 0.0016972 | -0.75483 | 6.3096 | 0.0050916 | 5.5599 |  | 9.5599 | 4 | 9.5599 | 34.7492 | 17.3746 | 20 | 20 | -2.6254 | 383.1415
530 | 8.8333 | 2.0781 | 10.6499 | 2 | 10.4 | 34.7035 | 0 | -0.2499 | 125.9423 | 0.0017124 | -0.74969 | 6.2971 | 0.0051371 | 5.5526 |  | 9.5526 | 4 | 9.5526 | 34.7035 | 17.3518 | 20 | 20 | -2.6482 | 380.4932
531 | 8.85 | 2.0776 | 10.6482 | 2 | 10.4 | 34.6586 | 0 | -0.24817 | 125.6941 | 0.0017273 | -0.74451 | 6.2847 | 0.0051818 | 5.5454 |  | 9.5454 | 4 | 9.5454 | 34.6586 | 17.3293 | 20 | 20 | -2.6707 | 377.8226
532 | 8.8667 | 2.077 | 10.6464 | 2 | 10.4 | 34.6146 | 0 | -0.24643 | 125.4477 | 0.0017419 | -0.73928 | 6.2724 | 0.0052257 | 5.5383 |  | 9.5383 | 4 | 9.5383 | 34.6146 | 17.3073 | 20 | 20 | -2.6927 | 375.1298
533 | 8.8833 | 2.0765 | 10.6447 | 2 | 10.4 | 34.5713 | 0 | -0.24467 | 125.203 | 0.0017563 | -0.73401 | 6.2602 | 0.0052688 | 5.5314 |  | 9.5314 | 4 | 9.5314 | 34.5713 | 17.2857 | 20 | 20 | -2.7143 | 372.4155
534 | 8.9 | 2.0759 | 10.6429 | 2 | 10.4 | 34.5289 | 0 | -0.2429 | 124.9601 | 0.0017704 | -0.7287 | 6.248 | 0.0053111 | 5.5246 |  | 9.5246 | 4 | 9.5246 | 34.5289 | 17.2644 | 20 | 20 | -2.7356 | 369.6799
535 | 8.9167 | 2.0753 | 10.6411 | 2 | 10.4 | 34.4872 | 0 | -0.24112 | 124.719 | 0.0017842 | -0.72335 | 6.236 | 0.0053527 | 5.518 |  | 9.518 | 4 | 9.518 | 34.4872 | 17.2436 | 20 | 20 | -2.7564 | 366.9235
536 | 8.9333 | 2.0748 | 10.6393 | 2 | 10.4 | 34.4464 | 0 | -0.23932 | 124.4797 | 0.0017978 | -0.71795 | 6.224 | 0.0053934 | 5.5114 |  | 9.5114 | 4 | 9.5114 | 34.4464 | 17.2232 | 20 | 20 | -2.7768 | 364.1467
537 | 8.95 | 2.0742 | 10.6375 | 2 | 10.4 | 34.4064 | 0 | -0.23751 | 124.2422 | 0.0018111 | -0.71252 | 6.2121 | 0.0054333 | 5.505 |  | 9.505 | 4 | 9.505 | 34.4064 | 17.2032 | 20 | 20 | -2.7968 | 361.3499
538 | 8.9667 | 2.0737 | 10.6357 | 2 | 10.4 | 34.3672 | 0 | -0.23568 | 124.0065 | 0.0018242 | -0.70705 | 6.2003 | 0.0054725 | 5.4987 |  | 9.4987 | 4 | 9.4987 | 34.3672 | 17.1836 | 20 | 20 | -2.8164 | 358.5335
539 | 8.9833 | 2.0731 | 10.6338 | 2 | 10.4 | 34.3288 | 0 | -0.23385 | 123.7727 | 0.0018369 | -0.70154 | 6.1886 | 0.0055108 | 5.4926 |  | 9.4926 | 4 | 9.4926 | 34.3288 | 17.1644 | 20 | 20 | -2.8356 | 355.6979
540 | 9 | 2.0725 | 10.632 | 2 | 10.4 | 34.2912 | 0 | -0.232 | 123.5407 | 0.0018495 | -0.69599 | 6.177 | 0.0055484 | 5.4866 |  | 9.4866 | 4 | 9.4866 | 34.2912 | 17.1456 | 20 | 20 | -2.8544 | 352.8435
541 | 9.0167 | 2.0719 | 10.6301 | 2 | 10.4 | 34.2544 | 0 | -0.23013 | 123.3105 | 0.0018617 | -0.6904 | 6.1655 | 0.0055852 | 5.4807 |  | 9.4807 | 4 | 9.4807 | 34.2544 | 17.1272 | 20 | 20 | -2.8728 | 349.9707
542 | 9.0333 | 2.0713 | 10.6283 | 2 | 10.4 | 34.2184 | 0 | -0.22826 | 123.0823 | 0.0018737 | -0.68478 | 6.1541 | 0.0056212 | 5.475 |  | 9.475 | 4 | 9.475 | 34.2184 | 17.1092 | 20 | 20 | -2.8908 | 347.08
543 | 9.05 | 2.0707 | 10.6264 | 2 | 10.4 | 34.1833 | 0 | -0.22638 | 122.8559 | 0.0018854 | -0.67913 | 6.1428 | 0.0056563 | 5.4693 |  | 9.4693 | 4 | 9.4693 | 34.1833 | 17.0916 | 20 | 20 | -2.9084 | 344.1716
544 | 9.0667 | 2.0701 | 10.6245 | 2 | 10.4 | 34.1489 | 0 | -0.22448 | 122.6314 | 0.0018969 | -0.67344 | 6.1316 | 0.0056908 | 5.4638 |  | 9.4638 | 4 | 9.4638 | 34.1489 | 17.0745 | 20 | 20 | -2.9255 | 341.2461
545 | 9.0833 | 2.0696 | 10.6226 | 2 | 10.4 | 34.1153 | 0 | -0.22257 | 122.4089 | 0.0019081 | -0.66771 | 6.1204 | 0.0057244 | 5.4585 |  | 9.4585 | 4 | 9.4585 | 34.1153 | 17.0577 | 20 | 20 | -2.9423 | 338.3037
546 | 9.1 | 2.069 | 10.6207 | 2 | 10.4 | 34.0826 | 0 | -0.22065 | 122.1882 | 0.0019191 | -0.66195 | 6.1094 | 0.0057572 | 5.4532 |  | 9.4532 | 4 | 9.4532 | 34.0826 | 17.0413 | 20 | 20 | -2.9587 | 335.345
547 | 9.1167 | 2.0684 | 10.6187 | 2 | 10.4 | 34.0506 | 0 | -0.21872 | 121.9695 | 0.0019298 | -0.65617 | 6.0985 | 0.0057893 | 5.4481 |  | 9.4481 | 4 | 9.4481 | 34.0506 | 17.0253 | 20 | 20 | -2.9747 | 332.3703
548 | 9.1333 | 2.0677 | 10.6168 | 2 | 10.4 | 34.0194 | 0 | -0.21678 | 121.7527 | 0.0019402 | -0.65034 | 6.0876 | 0.0058205 | 5.4431 |  | 9.4431 | 4 | 9.4431 | 34.0194 | 17.0097 | 20 | 20 | -2.9903 | 329.38
549 | 9.15 | 2.0671 | 10.6148 | 2 | 10.4 | 33.9891 | 0 | -0.21483 | 121.5379 | 0.0019503 | -0.64449 | 6.0769 | 0.005851 | 5.4383 |  | 9.4383 | 4 | 9.4383 | 33.9891 | 16.9945 | 20 | 20 | -3.0055 | 326.3746
550 | 9.1667 | 2.0665 | 10.6129 | 2 | 10.4 | 33.9595 | 0 | -0.21287 | 121.325 | 0.0019603 | -0.63861 | 6.0662 | 0.0058808 | 5.4335 |  | 9.4335 | 4 | 9.4335 | 33.9595 | 16.9797 | 20 | 20 | -3.0203 | 323.3543
551 | 9.1833 | 2.0659 | 10.6109 | 2 | 10.4 | 33.9307 | 0 | -0.2109 | 121.1141 | 0.0019699 | -0.6327 | 6.0557 | 0.0059097 | 5.4289 |  | 9.4289 | 4 | 9.4289 | 33.9307 | 16.9653 | 20 | 20 | -3.0347 | 320.3197
552 | 9.2 | 2.0653 | 10.6089 | 2 | 10.4 | 33.9027 | 0 | -0.20892 | 120.9052 | 0.0019793 | -0.62677 | 6.0453 | 0.0059379 | 5.4244 |  | 9.4244 | 4 | 9.4244 | 33.9027 | 16.9513 | 20 | 20 | -3.0487 | 317.271
553 | 9.2167 | 2.0647 | 10.6069 | 2 | 10.4 | 33.8755 | 0 | -0.20693 | 120.6982 | 0.0019884 | -0.6208 | 6.0349 | 0.0059653 | 5.4201 |  | 9.4201 | 4 | 9.4201 | 33.8755 | 16.9377 | 20 | 20 | -3.0623 | 314.2088
554 | 9.2333 | 2.064 | 10.6049 | 2 | 10.4 | 33.8491 | 0 | -0.20494 | 120.4933 | 0.0019973 | -0.61481 | 6.0247 | 0.0059919 | 5.4158 |  | 9.4158 | 4 | 9.4158 | 33.8491 | 16.9245 | 20 | 20 | -3.0755 | 311.1333
555 | 9.25 | 2.0634 | 10.6029 | 2 | 10.4 | 33.8234 | 0 | -0.20293 | 120.2904 | 0.0020059 | -0.60879 | 6.0145 | 0.0060177 | 5.4117 |  | 9.4117 | 4 | 9.4117 | 33.8234 | 16.9117 | 20 | 20 | -3.0883 | 308.045
556 | 9.2667 | 2.0628 | 10.6009 | 2 | 10.4 | 33.7985 | 0 | -0.20092 | 120.0895 | 0.0020143 | -0.60275 | 6.0045 | 0.0060428 | 5.4078 |  | 9.4078 | 4 | 9.4078 | 33.7985 | 16.8993 | 20 | 20 | -3.1007 | 304.9443
557 | 9.2833 | 2.0622 | 10.5989 | 2 | 10.4 | 33.7745 | 0 | -0.19889 | 119.8906 | 0.0020224 | -0.59668 | 5.9945 | 0.0060672 | 5.4039 |  | 9.4039 | 4 | 9.4039 | 33.7745 | 16.8872 | 20 | 20 | -3.1128 | 301.8315
558 | 9.3 | 2.0615 | 10.5969 | 2 | 10.4 | 33.7512 | 0 | -0.19686 | 119.6937 | 0.0020302 | -0.59059 | 5.9847 | 0.0060907 | 5.4002 |  | 9.4002 | 4 | 9.4002 | 33.7512 | 16.8756 | 20 | 20 | -3.1244 | 298.7071
559 | 9.3167 | 2.0609 | 10.5948 | 2 | 10.4 | 33.7286 | 0 | -0.19483 | 119.4989 | 0.0020378 | -0.58448 | 5.9749 | 0.0061135 | 5.3966 |  | 9.3966 | 4 | 9.3966 | 33.7286 | 16.8643 | 20 | 20 | -3.1357 | 295.5714
560 | 9.3333 | 2.0602 | 10.5928 | 2 | 10.4 | 33.7069 | 0 | -0.19278 | 119.3061 | 0.0020452 | -0.57834 | 5.9653 | 0.0061356 | 5.3931 |  | 9.3931 | 4 | 9.3931 | 33.7069 | 16.8534 | 20 | 20 | -3.1466 | 292.4248
561 | 9.35 | 2.0596 | 10.5907 | 2 | 10.4 | 33.6859 | 0 | -0.19073 | 119.1154 | 0.0020523 | -0.57218 | 5.9558 | 0.0061568 | 5.3897 |  | 9.3897 | 4 | 9.3897 | 33.6859 | 16.8429 | 20 | 20 | -3.1571 | 289.2678
562 | 9.3667 | 2.059 | 10.5887 | 2 | 10.4 | 33.6657 | 0 | -0.18867 | 118.9267 | 0.0020591 | -0.56601 | 5.9463 | 0.0061774 | 5.3865 |  | 9.3865 | 4 | 9.3865 | 33.6657 | 16.8328 | 20 | 20 | -3.1672 | 286.1006
563 | 9.3833 | 2.0583 | 10.5866 | 2 | 10.4 | 33.6462 | 0 | -0.1866 | 118.7401 | 0.0020657 | -0.55981 | 5.937 | 0.0061972 | 5.3834 |  | 9.3834 | 4 | 9.3834 | 33.6462 | 16.8231 | 20 | 20 | -3.1769 | 282.9237
564 | 9.4 | 2.0577 | 10.5845 | 2 | 10.4 | 33.6275 | 0 | -0.18453 | 118.5556 | 0.0020721 | -0.55359 | 5.9278 | 0.0062162 | 5.3804 |  | 9.3804 | 4 | 9.3804 | 33.6275 | 16.8138 | 20 | 20 | -3.1862 | 279.7375
565 | 9.4167 | 2.057 | 10.5825 | 2 | 10.4 | 33.6096 | 0 | -0.18245 | 118.3731 | 0.0020782 | -0.54736 | 5.9187 | 0.0062345 | 5.3775 |  | 9.3775 | 4 | 9.3775 | 33.6096 | 16.8048 | 20 | 20 | -3.1952 | 276.5422
566 | 9.4333 | 2.0564 | 10.5804 | 2 | 10.4 | 33.5924 | 0 | -0.18037 | 118.1927 | 0.002084 | -0.54111 | 5.9096 | 0.006252 | 5.3748 |  | 9.3748 | 4 | 9.3748 | 33.5924 | 16.7962 | 20 | 20 | -3.2038 | 273.3384
567 | 9.45 | 2.0557 | 10.5783 | 2 | 10.4 | 33.576 | 0 | -0.17828 | 118.0145 | 0.0020896 | -0.53484 | 5.9007 | 0.0062688 | 5.3722 |  | 9.3722 | 4 | 9.3722 | 33.576 | 16.788 | 20 | 20 | -3.212 | 270.1264
568 | 9.4667 | 2.0551 | 10.5762 | 2 | 10.4 | 33.5603 | 0 | -0.17618 | 117.8383 | 0.002095 | -0.52855 | 5.8919 | 0.0062849 | 5.3696 |  | 9.3696 | 4 | 9.3696 | 33.5603 | 16.7801 | 20 | 20 | -3.2199 | 266.9066
569 | 9.4833 | 2.0544 | 10.5741 | 2 | 10.4 | 33.5454 | 0 | -0.17408 | 117.6642 | 0.0021001 | -0.52225 | 5.8832 | 0.0063003 | 5.3673 |  | 9.3673 | 4 | 9.3673 | 33.5454 | 16.7727 | 20 | 20 | -3.2273 | 263.6792
570 | 9.5 | 2.0537 | 10.572 | 2 | 10.4 | 33.5312 | 0 | -0.17198 | 117.4922 | 0.002105 | -0.51594 | 5.8746 | 0.0063149 | 5.365 |  | 9.365 | 4 | 9.365 | 33.5312 | 16.7656 | 20 | 20 | -3.2344 | 260.4448
571 | 9.5167 | 2.0531 | 10.5699 | 2 | 10.4 | 33.5177 | 0 | -0.16987 | 117.3223 | 0.0021096 | -0.50961 | 5.8661 | 0.0063287 | 5.3628 |  | 9.3628 | 4 | 9.3628 | 33.5177 | 16.7589 | 20 | 20 | -3.2411 | 257.2037
572 | 9.5333 | 2.0524 | 10.5678 | 2 | 10.4 | 33.505 | 0 | -0.16776 | 117.1546 | 0.002114 | -0.50327 | 5.8577 | 0.0063419 | 5.3608 |  | 9.3608 | 4 | 9.3608 | 33.505 | 16.7525 | 20 | 20 | -3.2475 | 253.9562
573 | 9.55 | 2.0518 | 10.5656 | 2 | 10.4 | 33.4931 | 0 | -0.16564 | 116.989 | 0.0021181 | -0.49691 | 5.8494 | 0.0063543 | 5.3589 |  | 9.3589 | 4 | 9.3589 | 33.4931 | 16.7465 | 20 | 20 | -3.2535 | 250.7027
574 | 9.5667 | 2.0511 | 10.5635 | 2 | 10.4 | 33.4818 | 0 | -0.16352 | 116.8254 | 0.002122 | -0.49055 | 5.8413 | 0.006366 | 5.3571 |  | 9.3571 | 4 | 9.3571 | 33.4818 | 16.7409 | 20 | 20 | -3.2591 | 247.4436
575 | 9.5833 | 2.0504 | 10.5614 | 2 | 10.4 | 33.4713 | 0 | -0.16139 | 116.664 | 0.0021257 | -0.48417 | 5.8332 | 0.006377 | 5.3554 |  | 9.3554 | 4 | 9.3554 | 33.4713 | 16.7357 | 20 | 20 | -3.2643 | 244.1793
576 | 9.6 | 2.0498 | 10.5593 | 2 | 10.4 | 33.4615 | 0 | -0.15926 | 116.5048 | 0.0021291 | -0.47778 | 5.8252 | 0.0063873 | 5.3538 |  | 9.3538 | 4 | 9.3538 | 33.4615 | 16.7308 | 20 | 20 | -3.2692 | 240.9101
577 | 9.6167 | 2.0491 | 10.5571 | 2 | 10.4 | 33.4525 | 0 | -0.15713 | 116.3477 | 0.0021323 | -0.47139 | 5.8174 | 0.0063969 | 5.3524 |  | 9.3524 | 4 | 9.3524 | 33.4525 | 16.7262 | 20 | 20 | -3.2738 | 237.6363
578 | 9.6333 | 2.0484 | 10.555 | 2 | 10.4 | 33.4441 | 0 | -0.15499 | 116.1927 | 0.0021352 | -0.46498 | 5.8096 | 0.0064057 | 5.3511 |  | 9.3511 | 4 | 9.3511 | 33.4441 | 16.7221 | 20 | 20 | -3.2779 | 234.3583
579 | 9.65 | 2.0478 | 10.5529 | 2 | 10.4 | 33.4365 | 0 | -0.15286 | 116.0398 | 0.002138 | -0.45857 | 5.802 | 0.0064139 | 5.3498 |  | 9.3498 | 4 | 9.3498 | 33.4365 | 16.7182 | 20 | 20 | -3.2818 | 231.0766
580 | 9.6667 | 2.0471 | 10.5507 | 2 | 10.4 | 33.4296 | 0 | -0.15071 | 115.8891 | 0.0021405 | -0.45214 | 5.7945 | 0.0064214 | 5.3487 |  | 9.3487 | 4 | 9.3487 | 33.4296 | 16.7148 | 20 | 20 | -3.2852 | 227.7914
581 | 9.6833 | 2.0464 | 10.5486 | 2 | 10.4 | 33.4234 | 0 | -0.14857 | 115.7405 | 0.0021427 | -0.44572 | 5.787 | 0.0064281 | 5.3477 |  | 9.3477 | 4 | 9.3477 | 33.4234 | 16.7117 | 20 | 20 | -3.2883 | 224.5031
582 | 9.7 | 2.0458 | 10.5464 | 2 | 10.4 | 33.4179 | 0 | -0.14643 | 115.5941 | 0.0021447 | -0.43928 | 5.7797 | 0.0064342 | 5.3469 |  | 9.3469 | 4 | 9.3469 | 33.4179 | 16.7089 | 20 | 20 | -3.2911 | 221.212
583 | 9.7167 | 2.0451 | 10.5443 | 2 | 10.4 | 33.413 | 0 | -0.14428 | 115.4498 | 0.0021465 | -0.43284 | 5.7725 | 0.0064396 | 5.3461 |  | 9.3461 | 4 | 9.3461 | 33.413 | 16.7065 | 20 | 20 | -3.2935 | 217.9185
584 | 9.7333 | 2.0444 | 10.5421 | 2 | 10.4 | 33.4089 | 0 | -0.14213 | 115.3077 | 0.0021481 | -0.4264 | 5.7654 | 0.0064443 | 5.3454 |  | 9.3454 | 4 | 9.3454 | 33.4089 | 16.7045 | 20 | 20 | -3.2955 | 214.623
585 | 9.75 | 2.0437 | 10.54 | 2 | 10.4 | 33.4055 | 0 | -0.13998 | 115.1677 | 0.0021494 | -0.41995 | 5.7584 | 0.0064483 | 5.3449 |  | 9.3449 | 4 | 9.3449 | 33.4055 | 16.7028 | 20 | 20 | -3.2972 | 211.3257
586 | 9.7667 | 2.0431 | 10.5378 | 2 | 10.4 | 33.4028 | 0 | -0.13783 | 115.0299 | 0.0021506 | -0.4135 | 5.7515 | 0.0064517 | 5.3444 |  | 9.3444 | 4 | 9.3444 | 33.4028 | 16.7014 | 20 | 20 | -3.2986 | 208.0271
587 | 9.7833 | 2.0424 | 10.5357 | 2 | 10.4 | 33.4007 | 0 | -0.13568 | 114.8942 | 0.0021514 | -0.40704 | 5.7447 | 0.0064543 | 5.3441 |  | 9.3441 | 4 | 9.3441 | 33.4007 | 16.7004 | 20 | 20 | -3.2996 | 204.7275
588 | 9.8 | 2.0417 | 10.5335 | 2 | 10.4 | 33.3994 | 0 | -0.13353 | 114.7607 | 0.0021521 | -0.40059 | 5.738 | 0.0064563 | 5.3439 |  | 9.3439 | 4 | 9.3439 | 33.3994 | 16.6997 | 20 | 20 | -3.3003 | 201.4272
589 | 9.8167 | 2.0411 | 10.5314 | 2 | 10.4 | 33.3987 | 0 | -0.13138 | 114.6293 | 0.0021526 | -0.39413 | 5.7315 | 0.0064577 | 5.3438 |  | 9.3438 | 4 | 9.3438 | 33.3987 | 16.6993 | 20 | 20 | -3.3007 | 198.1265
590 | 9.8333 | 2.0404 | 10.5292 | 2 | 10.4 | 33.3987 | 0 | -0.12922 | 114.5001 | 0.0021528 | -0.38767 | 5.725 | 0.0064583 | 5.3438 |  | 9.3438 | 4 | 9.3438 | 33.3987 | 16.6993 | 20 | 20 | -3.3007 | 194.8259
591 | 9.85 | 2.0397 | 10.5271 | 2 | 10.4 | 33.3993 | 0 | -0.12707 | 114.373 | 0.0021528 | -0.38121 | 5.7186 | 0.0064584 | 5.3439 |  | 9.3439 | 4 | 9.3439 | 33.3993 | 16.6997 | 20 | 20 | -3.3003 | 191.5255
592 | 9.8667 | 2.039 | 10.5249 | 2 | 10.4 | 33.4007 | 0 | -0.12492 | 114.2481 | 0.0021526 | -0.37476 | 5.7124 | 0.0064577 | 5.3441 |  | 9.3441 | 4 | 9.3441 | 33.4007 | 16.7003 | 20 | 20 | -3.2997 | 188.2259
593 | 9.8833 | 2.0384 | 10.5228 | 2 | 10.4 | 33.4026 | 0 | -0.12277 | 114.1253 | 0.0021521 | -0.3683 | 5.7063 | 0.0064564 | 5.3444 |  | 9.3444 | 4 | 9.3444 | 33.4026 | 16.7013 | 20 | 20 | -3.2987 | 184.9272
594 | 9.9 | 2.0377 | 10.5206 | 2 | 10.4 | 33.4053 | 0 | -0.12061 | 114.0047 | 0.0021515 | -0.36184 | 5.7002 | 0.0064545 | 5.3448 |  | 9.3448 | 4 | 9.3448 | 33.4053 | 16.7026 | 20 | 20 | -3.2974 | 181.6298
595 | 9.9167 | 2.037 | 10.5185 | 2 | 10.4 | 33.4086 | 0 | -0.11846 | 113.8862 | 0.0021506 | -0.35539 | 5.6943 | 0.0064519 | 5.3454 |  | 9.3454 | 4 | 9.3454 | 33.4086 | 16.7043 | 20 | 20 | -3.2957 | 178.3341
596 | 9.9333 | 2.0363 | 10.5163 | 2 | 10.4 | 33.4125 | 0 | -0.11631 | 113.7699 | 0.0021496 | -0.34894 | 5.6885 | 0.0064487 | 5.346 |  | 9.346 | 4 | 9.346 | 33.4125 | 16.7062 | 20 | 20 | -3.2938 | 175.0404
597 | 9.95 | 2.0357 | 10.5142 | 2 | 10.4 | 33.4171 | 0 | -0.11417 | 113.6557 | 0.0021483 | -0.3425 | 5.6828 | 0.0064448 | 5.3467 |  | 9.3467 | 4 | 9.3467 | 33.4171 | 16.7085 | 20 | 20 | -3.2915 | 171.7489
598 | 9.9667 | 2.035 | 10.512 | 2 | 10.4 | 33.4223 | 0 | -0.11202 | 113.5437 | 0.0021468 | -0.33606 | 5.6772 | 0.0064404 | 5.3476 |  | 9.3476 | 4 | 9.3476 | 33.4223 | 16.7111 | 20 | 20 | -3.2889 | 168.46
599 | 9.9833 | 2.0343 | 10.5099 | 2 | 10.4 | 33.4281 | 0 | -0.10987 | 113.4338 | 0.0021451 | -0.32962 | 5.6717 | 0.0064353 | 5.3485 |  | 9.3485 | 4 | 9.3485 | 33.4281 | 16.7141 | 20 | 20 | -3.2859 | 165.1741
600 | 10 | 2.0337 | 10.5077 | 2 | 10.4 | 33.4346 | 0 | -0.10773 | 113.3261 | 0.0021432 | -0.32319 | 5.6663 | 0.0064295 | 5.3495 |  | 9.3495 | 4 | 9.3495 | 33.4346 | 16.7173 | 20 | 20 | -3.2827 | 161.8914
601 | 10.0167 | 2.033 | 10.5056 | 2 | 10.4 | 33.4417 | 0 | -0.10559 | 113.2205 | 0.0021411 | -0.31677 | 5.661 | 0.0064232 | 5.3507 |  | 9.3507 | 4 | 9.3507 | 33.4417 | 16.7209 | 20 | 20 | -3.2791 | 158.6123
602 | 10.0333 | 2.0323 | 10.5035 | 2 | 10.4 | 33.4495 | 0 | -0.10345 | 113.1171 | 0.0021387 | -0.31035 | 5.6559 | 0.0064162 | 5.3519 |  | 9.3519 | 4 | 9.3519 | 33.4495 | 16.7247 | 20 | 20 | -3.2753 | 155.337
603 | 10.05 | 2.0317 | 10.5013 | 2 | 10.4 | 33.4578 | 0 | -0.10132 | 113.0158 | 0.0021362 | -0.30395 | 5.6508 | 0.0064087 | 5.3533 |  | 9.3533 | 4 | 9.3533 | 33.4578 | 16.7289 | 20 | 20 | -3.2711 | 152.0659
604 | 10.0667 | 2.031 | 10.4992 | 2 | 10.4 | 33.4668 | 0 | -0.099182 | 112.9166 | 0.0021335 | -0.29755 | 5.6458 | 0.0064005 | 5.3547 |  | 9.3547 | 4 | 9.3547 | 33.4668 | 16.7334 | 20 | 20 | -3.2666 | 148.7993
605 | 10.0833 | 2.0303 | 10.4971 | 2 | 10.4 | 33.4763 | 0 | -0.097051 | 112.8195 | 0.0021306 | -0.29115 | 5.641 | 0.0063917 | 5.3562 |  | 9.3562 | 4 | 9.3562 | 33.4763 | 16.7382 | 20 | 20 | -3.2618 | 145.5375
606 | 10.1 | 2.0297 | 10.4949 | 2 | 10.4 | 33.4865 | 0 | -0.094924 | 112.7246 | 0.0021275 | -0.28477 | 5.6362 | 0.0063824 | 5.3578 |  | 9.3578 | 4 | 9.3578 | 33.4865 | 16.7433 | 20 | 20 | -3.2567 | 142.2808
607 | 10.1167 | 2.029 | 10.4928 | 2 | 10.4 | 33.4973 | 0 | -0.0928 | 112.6318 | 0.0021241 | -0.2784 | 5.6316 | 0.0063724 | 5.3596 |  | 9.3596 | 4 | 9.3596 | 33.4973 | 16.7486 | 20 | 20 | -3.2514 | 139.0294
608 | 10.1333 | 2.0283 | 10.4907 | 2 | 10.4 | 33.5086 | 0 | -0.090679 | 112.5411 | 0.0021206 | -0.27204 | 5.6271 | 0.0063619 | 5.3614 |  | 9.3614 | 4 | 9.3614 | 33.5086 | 16.7543 | 20 | 20 | -3.2457 | 135.7837
609 | 10.15 | 2.0277 | 10.4886 | 2 | 10.4 | 33.5206 | 0 | -0.088562 | 112.4526 | 0.0021169 | -0.26569 | 5.6226 | 0.0063508 | 5.3633 |  | 9.3633 | 4 | 9.3633 | 33.5206 | 16.7603 | 20 | 20 | -3.2397 | 132.544
610 | 10.1667 | 2.027 | 10.4864 | 2 | 10.4 | 33.5331 | 0 | -0.086449 | 112.3661 | 0.002113 | -0.25935 | 5.6183 | 0.0063391 | 5.3653 |  | 9.3653 | 4 | 9.3653 | 33.5331 | 16.7666 | 20 | 20 | -3.2334 | 129.3105
611 | 10.1833 | 2.0264 | 10.4843 | 2 | 10.4 | 33.5462 | 0 | -0.08434 | 112.2818 | 0.0021089 | -0.25302 | 5.6141 | 0.0063268 | 5.3674 |  | 9.3674 | 4 | 9.3674 | 33.5462 | 16.7731 | 20 | 20 | -3.2269 | 126.0837
612 | 10.2 | 2.0257 | 10.4822 | 2 | 10.4 | 33.5599 | 0 | -0.082235 | 112.1995 | 0.0021047 | -0.24671 | 5.61 | 0.006314 | 5.3696 |  | 9.3696 | 4 | 9.3696 | 33.5599 | 16.78 | 20 | 20 | -3.22 | 122.8636
613 | 10.2167 | 2.025 | 10.4801 | 2 | 10.4 | 33.5742 | 0 | -0.080135 | 112.1194 | 0.0021002 | -0.24041 | 5.606 | 0.0063006 | 5.3719 |  | 9.3719 | 4 | 9.3719 | 33.5742 | 16.7871 | 20 | 20 | -3.2129 | 119.6507
614 | 10.2333 | 2.0244 | 10.478 | 2 | 10.4 | 33.589 | 0 | -0.07804 | 112.0414 | 0.0020956 | -0.23412 | 5.6021 | 0.0062867 | 5.3742 |  | 9.3742 | 4 | 9.3742 | 33.589 | 16.7945 | 20 | 20 | -3.2055 | 116.4452
615 | 10.25 | 2.0237 | 10.4759 | 2 | 10.4 | 33.6043 | 0 | -0.075949 | 111.9654 | 0.0020907 | -0.22785 | 5.5983 | 0.0062722 | 5.3767 |  | 9.3767 | 4 | 9.3767 | 33.6043 | 16.8022 | 20 | 20 | -3.1978 | 113.2473
616 | 10.2667 | 2.0231 | 10.4739 | 2 | 10.4 | 33.6203 | 0 | -0.073863 | 111.8915 | 0.0020857 | -0.22159 | 5.5946 | 0.0062571 | 5.3792 |  | 9.3792 | 4 | 9.3792 | 33.6203 | 16.8101 | 20 | 20 | -3.1899 | 110.0575
617 | 10.2833 | 2.0224 | 10.4718 | 2 | 10.4 | 33.6368 | 0 | -0.071783 | 111.8198 | 0.0020805 | -0.21535 | 5.591 | 0.0062416 | 5.3819 |  | 9.3819 | 4 | 9.3819 | 33.6368 | 16.8184 | 20 | 20 | -3.1816 | 106.8759
618 | 10.3 | 2.0218 | 10.4697 | 2 | 10.4 | 33.6538 | 0 | -0.069708 | 111.7501 | 0.0020751 | -0.20912 | 5.5875 | 0.0062254 | 5.3846 |  | 9.3846 | 4 | 9.3846 | 33.6538 | 16.8269 | 20 | 20 | -3.1731 | 103.7028
619 | 10.3167 | 2.0211 | 10.4676 | 2 | 10.4 | 33.6713 | 0 | -0.067638 | 111.6824 | 0.0020696 | -0.20291 | 5.5841 | 0.0062088 | 5.3874 |  | 9.3874 | 4 | 9.3874 | 33.6713 | 16.8357 | 20 | 20 | -3.1643 | 100.5384
620 | 10.3333 | 2.0205 | 10.4656 | 2 | 10.4 | 33.6894 | 0 | -0.065574 | 111.6168 | 0.0020639 | -0.19672 | 5.5808 | 0.0061916 | 5.3903 |  | 9.3903 | 4 | 9.3903 | 33.6894 | 16.8447 | 20 | 20 | -3.1553 | 97.3831
621 | 10.35 | 2.0198 | 10.4635 | 2 | 10.4 | 33.7081 | 0 | -0.063516 | 111.5533 | 0.002058 | -0.19055 | 5.5777 | 0.0061739 | 5.3933 |  | 9.3933 | 4 | 9.3933 | 33.7081 | 16.854 | 20 | 20 | -3.146 | 94.2372
622 | 10.3667 | 2.0192 | 10.4615 | 2 | 10.4 | 33.7272 | 0 | -0.061464 | 111.4919 | 0.0020519 | -0.18439 | 5.5746 | 0.0061557 | 5.3964 |  | 9.3964 | 4 | 9.3964 | 33.7272 | 16.8636 | 20 | 20 | -3.1364 | 91.1008
623 | 10.3833 | 2.0186 | 10.4594 | 2 | 10.4 | 33.7469 | 0 | -0.059419 | 111.4324 | 0.0020456 | -0.17826 | 5.5716 | 0.0061369 | 5.3995 |  | 9.3995 | 4 | 9.3995 | 33.7469 | 16.8734 | 20 | 20 | -3.1266 | 87.9742
624 | 10.4 | 2.0179 | 10.4574 | 2 | 10.4 | 33.7671 | 0 | -0.057379 | 111.3751 | 0.0020392 | -0.17214 | 5.5688 | 0.0061177 | 5.4027 |  | 9.4027 | 4 | 9.4027 | 33.7671 | 16.8835 | 20 | 20 | -3.1165 | 84.8578
625 | 10.4167 | 2.0173 | 10.4553 | 2 | 10.4 | 33.7878 | 0 | -0.055347 | 111.3197 | 0.0020326 | -0.16604 | 5.566 | 0.0060979 | 5.406 |  | 9.406 | 4 | 9.406 | 33.7878 | 16.8939 | 20 | 20 | -3.1061 | 81.7517
626 | 10.4333 | 2.0167 | 10.4533 | 2 | 10.4 | 33.809 | 0 | -0.053321 | 111.2664 | 0.0020259 | -0.15996 | 5.5633 | 0.0060777 | 5.4094 |  | 9.4094 | 4 | 9.4094 | 33.809 | 16.9045 | 20 | 20 | -3.0955 | 78.6562
627 | 10.45 | 2.016 | 10.4513 | 2 | 10.4 | 33.8307 | 0 | -0.051302 | 111.2151 | 0.002019 | -0.15391 | 5.5608 | 0.006057 | 5.4129 |  | 9.4129 | 4 | 9.4129 | 33.8307 | 16.9153 | 20 | 20 | -3.0847 | 75.5715
628 | 10.4667 | 2.0154 | 10.4493 | 2 | 10.4 | 33.8529 | 0 | -0.04929 | 111.1658 | 0.0020119 | -0.14787 | 5.5583 | 0.0060357 | 5.4165 |  | 9.4165 | 4 | 9.4165 | 33.8529 | 16.9264 | 20 | 20 | -3.0736 | 72.4979
629 | 10.4833 | 2.0148 | 10.4473 | 2 | 10.4 | 33.8755 | 0 | -0.047285 | 111.1185 | 0.0020047 | -0.14186 | 5.5559 | 0.006014 | 5.4201 |  | 9.4201 | 4 | 9.4201 | 33.8755 | 16.9378 | 20 | 20 | -3.0622 | 69.4357
630 | 10.5 | 2.0142 | 10.4453 | 2 | 10.4 | 33.8987 | 0 | -0.045288 | 111.0732 | 0.0019973 | -0.13586 | 5.5537 | 0.0059918 | 5.4238 |  | 9.4238 | 4 | 9.4238 | 33.8987 | 16.9493 | 20 | 20 | -3.0507 | 66.385
631 | 10.5167 | 2.0135 | 10.4433 | 2 | 10.4 | 33.9223 | 0 | -0.043298 | 111.0299 | 0.0019897 | -0.12989 | 5.5515 | 0.0059692 | 5.4276 |  | 9.4276 | 4 | 9.4276 | 33.9223 | 16.9612 | 20 | 20 | -3.0388 | 63.3462
632 | 10.5333 | 2.0129 | 10.4413 | 2 | 10.4 | 33.9464 | 0 | -0.041316 | 110.9886 | 0.001982 | -0.12395 | 5.5494 | 0.0059461 | 5.4314 |  | 9.4314 | 4 | 9.4314 | 33.9464 | 16.9732 | 20 | 20 | -3.0268 | 60.3194
633 | 10.55 | 2.0123 | 10.4393 | 2 | 10.4 | 33.971 | 0 | -0.039342 | 110.9493 | 0.0019742 | -0.11803 | 5.5475 | 0.0059225 | 5.4354 |  | 9.4354 | 4 | 9.4354 | 33.971 | 16.9855 | 20 | 20 | -3.0145 | 57.3049
634 | 10.5667 | 2.0117 | 10.4374 | 2 | 10.4 | 33.996 | 0 | -0.037376 | 110.9119 | 0.0019661 | -0.11213 | 5.5456 | 0.0058984 | 5.4394 |  | 9.4394 | 4 | 9.4394 | 33.996 | 16.998 | 20 | 20 | -3.002 | 54.3029
635 | 10.5833 | 2.0111 | 10.4354 | 2 | 10.4 | 34.0215 | 0 | -0.035418 | 110.8765 | 0.001958 | -0.10625 | 5.5438 | 0.0058739 | 5.4434 |  | 9.4434 | 4 | 9.4434 | 34.0215 | 17.0108 | 20 | 20 | -2.9892 | 51.3137
636 | 10.6 | 2.0105 | 10.4335 | 2 | 10.4 | 34.0475 | 0 | -0.033468 | 110.843 | 0.0019497 | -0.1004 | 5.5422 | 0.005849 | 5.4476 |  | 9.4476 | 4 | 9.4476 | 34.0475 | 17.0237 | 20 | 20 | -2.9763 | 48.3374
637 | 10.6167 | 2.0099 | 10.4315 | 2 | 10.4 | 34.0739 | 0 | -0.031527 | 110.8115 | 0.0019412 | -0.094581 | 5.5406 | 0.0058236 | 5.4518 |  | 9.4518 | 4 | 9.4518 | 34.0739 | 17.0369 | 20 | 20 | -2.9631 | 45.3743
638 | 10.6333 | 2.0092 | 10.4296 | 2 | 10.4 | 34.1007 | 0 | -0.029594 | 110.7819 | 0.0019326 | -0.088783 | 5.5391 | 0.0057978 | 5.4561 |  | 9.4561 | 4 | 9.4561 | 34.1007 | 17.0503 | 20 | 20 | -2.9497 | 42.4247
639 | 10.65 | 2.0086 | 10.4277 | 2 | 10.4 | 34.1279 | 0 | -0.027671 | 110.7542 | 0.0019239 | -0.083012 | 5.5377 | 0.0057716 | 5.4605 |  | 9.4605 | 4 | 9.4605 | 34.1279 | 17.064 | 20 | 20 | -2.936 | 39.4886
640 | 10.6667 | 2.008 | 10.4258 | 2 | 10.4 | 34.1556 | 0 | -0.025756 | 110.7285 | 0.001915 | -0.077267 | 5.5364 | 0.0057449 | 5.4649 |  | 9.4649 | 4 | 9.4649 | 34.1556 | 17.0778 | 20 | 20 | -2.9222 | 36.5665
641 | 10.6833 | 2.0075 | 10.4238 | 2 | 10.4 | 34.1837 | 0 | -0.02385 | 110.7046 | 0.0019059 | -0.071549 | 5.5352 | 0.0057178 | 5.4694 |  | 9.4694 | 4 | 9.4694 | 34.1837 | 17.0919 | 20 | 20 | -2.9081 | 33.6583
642 | 10.7 | 2.0069 | 10.422 | 2 | 10.4 | 34.2123 | 0 | -0.021953 | 110.6827 | 0.0018968 | -0.065859 | 5.5341 | 0.0056903 | 5.474 |  | 9.474 | 4 | 9.474 | 34.2123 | 17.1061 | 20 | 20 | -2.8939 | 30.7645
643 | 10.7167 | 2.0063 | 10.4201 | 2 | 10.4 | 34.2412 | 0 | -0.020065 | 110.6626 | 0.0018875 | -0.060196 | 5.5331 | 0.0056624 | 5.4786 |  | 9.4786 | 4 | 9.4786 | 34.2412 | 17.1206 | 20 | 20 | -2.8794 | 27.8851
644 | 10.7333 | 2.0057 | 10.4182 | 2 | 10.4 | 34.2706 | 0 | -0.018187 | 110.6444 | 0.001878 | -0.054562 | 5.5322 | 0.0056341 | 5.4833 |  | 9.4833 | 4 | 9.4833 | 34.2706 | 17.1353 | 20 | 20 | -2.8647 | 25.0204
645 | 10.75 | 2.0051 | 10.4163 | 2 | 10.4 | 34.3003 | 0 | -0.016319 | 110.6281 | 0.0018684 | -0.048957 | 5.5314 | 0.0056053 | 5.4881 |  | 9.4881 | 4 | 9.4881 | 34.3003 | 17.1502 | 20 | 20 | -2.8498 | 22.1705
646 | 10.7667 | 2.0045 | 10.4145 | 2 | 10.4 | 34.3305 | 0 | -0.01446 | 110.6136 | 0.0018587 | -0.043381 | 5.5307 | 0.0055762 | 5.4929 |  | 9.4929 | 4 | 9.4929 | 34.3305 | 17.1652 | 20 | 20 | -2.8348 | 19.3358
647 | 10.7833 | 2.0039 | 10.4126 | 2 | 10.4 | 34.361 | 0 | -0.012611 | 110.601 | 0.0018489 | -0.037834 | 5.5301 | 0.0055467 | 5.4978 |  | 9.4978 | 4 | 9.4978 | 34.361 | 17.1805 | 20 | 20 | -2.8195 | 16.5163
648 | 10.8 | 2.0034 | 10.4108 | 2 | 10.4 | 34.3919 | 0 | -0.010772 | 110.5902 | 0.001839 | -0.032317 | 5.5295 | 0.0055169 | 5.5027 |  | 9.5027 | 4 | 9.5027 | 34.3919 | 17.196 | 20 | 20 | -2.804 | 13.7123
649 | 10.8167 | 2.0028 | 10.4089 | 2 | 10.4 | 34.4233 | 0 | -0.0089435 | 110.5813 | 0.0018289 | -0.026831 | 5.5291 | 0.0054866 | 5.5077 |  | 9.5077 | 4 | 9.5077 | 34.4233 | 17.2116 | 20 | 20 | -2.7884 | 10.9239
650 | 10.8333 | 2.0022 | 10.4071 | 2 | 10.4 | 34.4549 | 0 | -0.0071249 | 110.5742 | 0.0018187 | -0.021375 | 5.5287 | 0.005456 | 5.5128 |  | 9.5128 | 4 | 9.5128 | 34.4549 | 17.2275 | 20 | 20 | -2.7725 | 8.1514
651 | 10.85 | 2.0017 | 10.4053 | 2 | 10.4 | 34.487 | 0 | -0.0053166 | 110.5689 | 0.0018083 | -0.01595 | 5.5284 | 0.005425 | 5.5179 |  | 9.5179 | 4 | 9.5179 | 34.487 | 17.2435 | 20 | 20 | -2.7565 | 5.3949
652 | 10.8667 | 2.0011 | 10.4035 | 2 | 10.4 | 34.5194 | 0 | -0.0035187 | 110.5653 | 0.0017979 | -0.010556 | 5.5283 | 0.0053936 | 5.5231 |  | 9.5231 | 4 | 9.5231 | 34.5194 | 17.2597 | 20 | 20 | -2.7403 | 2.6546
653 | 10.8833 | 2.0005 | 10.4017 | 2 | 10.4 | 34.5522 | 0 | -0.0017314 | 110.5636 | 0.0017873 | -0.0051941 | 5.5282 | 0.0053619 | 5.5283 |  | 9.5283 | 4 | 9.5283 | 34.5522 | 17.2761 | 20 | 20 | -2.7239 | -0.069356
654 | 10.9 | 2 | 10.4 | 2 | 10.4 | 34.5853 | 0 | 4.5236e-05 | 110.5637 | 0.0017766 | 0.00013571 | 5.5282 | 0.0053298 | 5.5336 |  | 9.5336 | 4 | 9.5336 | 34.5853 | 17.2927 | 20 | 20 | -2.7073 | -2.7767
655 | 10.9167 | 1.9994 | 10.3982 | 2 | 10.4 | 34.6188 | 0 | 0.001811 | 110.5655 | 0.0017658 | 0.0054331 | 5.5283 | 0.0052974 | 5.539 |  | 9.539 | 4 | 9.539 | 34.6188 | 17.3094 | 20 | 20 | -2.6906 | -5.4673
656 | 10.9333 | 1.9989 | 10.3964 | 2 | 10.4 | 34.6526 | 0 | 0.0035659 | 110.569 | 0.0017549 | 0.010698 | 5.5285 | 0.0052647 | 5.5444 |  | 9.5444 | 4 | 9.5444 | 34.6526 | 17.3263 | 20 | 20 | -2.6737 | -8.141
657 | 10.95 | 1.9983 | 10.3947 | 2 | 10.4 | 34.6867 | 0 | 0.0053098 | 110.5743 | 0.0017439 | 0.015929 | 5.5287 | 0.0052316 | 5.5499 |  | 9.5499 | 4 | 9.5499 | 34.6867 | 17.3434 | 20 | 20 | -2.6566 | -10.7977
658 | 10.9667 | 1.9978 | 10.393 | 2 | 10.4 | 34.7212 | 0 | 0.0070425 | 110.5814 | 0.0017327 | 0.021128 | 5.5291 | 0.0051982 | 5.5554 |  | 9.5554 | 4 | 9.5554 | 34.7212 | 17.3606 | 20 | 20 | -2.6394 | -13.437
659 | 10.9833 | 1.9973 | 10.3912 | 2 | 10.4 | 34.756 | 0 | 0.008764 | 110.5901 | 0.0017215 | 0.026292 | 5.5295 | 0.0051645 | 5.561 |  | 9.561 | 4 | 9.561 | 34.756 | 17.378 | 20 | 20 | -2.622 | -16.059
660 | 11 | 1.9967 | 10.3895 | 2 | 10.4 | 34.7912 | 0 | 0.010474 | 110.6006 | 0.0017101 | 0.031423 | 5.53 | 0.0051304 | 5.5666 |  | 9.5666 | 4 | 9.5666 | 34.7912 | 17.3956 | 20 | 20 | -2.6044 | -18.6635
661 | 11.0167 | 1.9962 | 10.3878 | 2 | 10.4 | 34.8266 | 0 | 0.012173 | 110.6128 | 0.0016987 | 0.036519 | 5.5306 | 0.005096 | 5.5723 |  | 9.5723 | 4 | 9.5723 | 34.8266 | 17.4133 | 20 | 20 | -2.5867 | -21.2502
662 | 11.0333 | 1.9957 | 10.3861 | 2 | 10.4 | 34.8623 | 0 | 0.01386 | 110.6267 | 0.0016871 | 0.04158 | 5.5313 | 0.0050614 | 5.578 |  | 9.578 | 4 | 9.578 | 34.8623 | 17.4312 | 20 | 20 | -2.5688 | -23.819
663 | 11.05 | 1.9951 | 10.3845 | 2 | 10.4 | 34.8984 | 0 | 0.015535 | 110.6422 | 0.0016755 | 0.046606 | 5.5321 | 0.0050264 | 5.5837 |  | 9.5837 | 4 | 9.5837 | 34.8984 | 17.4492 | 20 | 20 | -2.5508 | -26.3698
664 | 11.0667 | 1.9946 | 10.3828 | 2 | 10.4 | 34.9347 | 0 | 0.017199 | 110.6594 | 0.0016637 | 0.051597 | 5.533 | 0.0049911 | 5.5896 |  | 9.5896 | 4 | 9.5896 | 34.9347 | 17.4674 | 20 | 20 | -2.5326 | -28.9024
665 | 11.0833 | 1.9941 | 10.3811 | 2 | 10.4 | 34.9714 | 0 | 0.018851 | 110.6782 | 0.0016519 | 0.056553 | 5.5339 | 0.0049556 | 5.5954 |  | 9.5954 | 4 | 9.5954 | 34.9714 | 17.4857 | 20 | 20 | -2.5143 | -31.4167
666 | 11.1 | 1.9936 | 10.3795 | 2 | 10.4 | 35.0083 | 0 | 0.020491 | 110.6987 | 0.0016399 | 0.061473 | 5.5349 | 0.0049197 | 5.6013 |  | 9.6013 | 4 | 9.6013 | 35.0083 | 17.5042 | 20 | 20 | -2.4958 | -33.9126
667 | 11.1167 | 1.9931 | 10.3779 | 2 | 10.4 | 35.0455 | 0 | 0.022119 | 110.7209 | 0.0016279 | 0.066356 | 5.536 | 0.0048836 | 5.6073 |  | 9.6073 | 4 | 9.6073 | 35.0455 | 17.5228 | 20 | 20 | -2.4772 | -36.3898
668 | 11.1333 | 1.9926 | 10.3763 | 2 | 10.4 | 35.083 | 0 | 0.023735 | 110.7446 | 0.0016157 | 0.071204 | 5.5372 | 0.0048472 | 5.6133 |  | 9.6133 | 4 | 9.6133 | 35.083 | 17.5415 | 20 | 20 | -2.4585 | -38.8483
669 | 11.15 | 1.9921 | 10.3747 | 2 | 10.4 | 35.1208 | 0 | 0.025338 | 110.7699 | 0.0016035 | 0.076014 | 5.5385 | 0.0048105 | 5.6193 |  | 9.6193 | 4 | 9.6193 | 35.1208 | 17.5604 | 20 | 20 | -2.4396 | -41.2879
670 | 11.1667 | 1.9916 | 10.3731 | 2 | 10.4 | 35.1588 | 0 | 0.026929 | 110.7969 | 0.0015912 | 0.080788 | 5.5398 | 0.0047736 | 5.6254 |  | 9.6254 | 4 | 9.6254 | 35.1588 | 17.5794 | 20 | 20 | -2.4206 | -43.7086
671 | 11.1833 | 1.9911 | 10.3715 | 2 | 10.4 | 35.1971 | 0 | 0.028508 | 110.8254 | 0.0015788 | 0.085524 | 5.5413 | 0.0047364 | 5.6315 |  | 9.6315 | 4 | 9.6315 | 35.1971 | 17.5985 | 20 | 20 | -2.4015 | -46.11
672 | 11.2 | 1.9906 | 10.3699 | 2 | 10.4 | 35.2356 | 0 | 0.030074 | 110.8554 | 0.0015663 | 0.090223 | 5.5428 | 0.0046989 | 5.6377 |  | 9.6377 | 4 | 9.6377 | 35.2356 | 17.6178 | 20 | 20 | -2.3822 | -48.4922
673 | 11.2167 | 1.9901 | 10.3684 | 2 | 10.4 | 35.2744 | 0 | 0.031628 | 110.8871 | 0.0015537 | 0.094884 | 5.5444 | 0.0046612 | 5.6439 |  | 9.6439 | 4 | 9.6439 | 35.2744 | 17.6372 | 20 | 20 | -2.3628 | -50.8551
674 | 11.2333 | 1.9896 | 10.3668 | 2 | 10.4 | 35.3134 | 0 | 0.033169 | 110.9202 | 0.0015411 | 0.099507 | 5.546 | 0.0046233 | 5.6501 |  | 9.6501 | 4 | 9.6501 | 35.3134 | 17.6567 | 20 | 20 | -2.3433 | -53.1984
675 | 11.25 | 1.9892 | 10.3653 | 2 | 10.4 | 35.3527 | 0 | 0.034698 | 110.9549 | 0.0015284 | 0.10409 | 5.5477 | 0.0045851 | 5.6564 |  | 9.6564 | 4 | 9.6564 | 35.3527 | 17.6763 | 20 | 20 | -2.3237 | -55.522
676 | 11.2667 | 1.9887 | 10.3638 | 2 | 10.4 | 35.3921 | 0 | 0.036213 | 110.9911 | 0.0015156 | 0.10864 | 5.5496 | 0.0045467 | 5.6627 |  | 9.6627 | 4 | 9.6627 | 35.3921 | 17.6961 | 20 | 20 | -2.3039 | -57.826
677 | 11.2833 | 1.9882 | 10.3623 | 2 | 10.4 | 35.4319 | 0 | 0.037716 | 111.0289 | 0.0015027 | 0.11315 | 5.5514 | 0.0045081 | 5.6691 |  | 9.6691 | 4 | 9.6691 | 35.4319 | 17.7159 | 20 | 20 | -2.2841 | -60.11
678 | 11.3 | 1.9877 | 10.3608 | 2 | 10.4 | 35.4718 | 0 | 0.039206 | 111.0681 | 0.0014897 | 0.11762 | 5.5534 | 0.0044692 | 5.6755 |  | 9.6755 | 4 | 9.6755 | 35.4718 | 17.7359 | 20 | 20 | -2.2641 | -62.3741
679 | 11.3167 | 1.9873 | 10.3593 | 2 | 10.4 | 35.512 | 0 | 0.040682 | 111.1087 | 0.0014767 | 0.12205 | 5.5554 | 0.0044301 | 5.6819 |  | 9.6819 | 4 | 9.6819 | 35.512 | 17.756 | 20 | 20 | -2.244 | -64.6182
680 | 11.3333 | 1.9868 | 10.3579 | 2 | 10.4 | 35.5523 | 0 | 0.042146 | 111.1509 | 0.0014636 | 0.12644 | 5.5575 | 0.0043908 | 5.6884 |  | 9.6884 | 4 | 9.6884 | 35.5523 | 17.7762 | 20 | 20 | -2.2238 | -66.842
681 | 11.35 | 1.9864 | 10.3564 | 2 | 10.4 | 35.5929 | 0 | 0.043596 | 111.1945 | 0.0014504 | 0.13079 | 5.5597 | 0.0043513 | 5.6949 |  | 9.6949 | 4 | 9.6949 | 35.5929 | 17.7965 | 20 | 20 | -2.2035 | -69.0455
682 | 11.3667 | 1.9859 | 10.355 | 2 | 10.4 | 35.6337 | 0 | 0.045034 | 111.2395 | 0.0014372 | 0.1351 | 5.562 | 0.0043117 | 5.7014 |  | 9.7014 | 4 | 9.7014 | 35.6337 | 17.8168 | 20 | 20 | -2.1832 | -71.2287
683 | 11.3833 | 1.9855 | 10.3535 | 2 | 10.4 | 35.6746 | 0 | 0.046457 | 111.286 | 0.0014239 | 0.13937 | 5.5643 | 0.0042718 | 5.7079 |  | 9.7079 | 4 | 9.7079 | 35.6746 | 17.8373 | 20 | 20 | -2.1627 | -73.3914
684 | 11.4 | 1.985 | 10.3521 | 2 | 10.4 | 35.7158 | 0 | 0.047868 | 111.3338 | 0.0014106 | 0.1436 | 5.5667 | 0.0042317 | 5.7145 |  | 9.7145 | 4 | 9.7145 | 35.7158 | 17.8579 | 20 | 20 | -2.1421 | -75.5335
685 | 11.4167 | 1.9846 | 10.3507 | 2 | 10.4 | 35.7571 | 0 | 0.049265 | 111.3831 | 0.0013971 | 0.1478 | 5.5692 | 0.0041914 | 5.7211 |  | 9.7211 | 4 | 9.7211 | 35.7571 | 17.8786 | 20 | 20 | -2.1214 | -77.6549
686 | 11.4333 | 1.9842 | 10.3494 | 2 | 10.4 | 35.7987 | 0 | 0.050649 | 111.4338 | 0.0013837 | 0.15195 | 5.5717 | 0.004151 | 5.7278 |  | 9.7278 | 4 | 9.7278 | 35.7987 | 17.8993 | 20 | 20 | -2.1007 | -79.7556
687 | 11.45 | 1.9837 | 10.348 | 2 | 10.4 | 35.8404 | 0 | 0.052019 | 111.4858 | 0.0013701 | 0.15606 | 5.5743 | 0.0041104 | 5.7345 |  | 9.7345 | 4 | 9.7345 | 35.8404 | 17.9202 | 20 | 20 | -2.0798 | -81.8354
688 | 11.4667 | 1.9833 | 10.3466 | 2 | 10.4 | 35.8822 | 0 | 0.053375 | 111.5392 | 0.0013565 | 0.16013 | 5.577 | 0.0040696 | 5.7412 |  | 9.7412 | 4 | 9.7412 | 35.8822 | 17.9411 | 20 | 20 | -2.0589 | -83.8943
689 | 11.4833 | 1.9829 | 10.3453 | 2 | 10.4 | 35.9242 | 0 | 0.054718 | 111.5939 | 0.0013429 | 0.16415 | 5.5797 | 0.0040286 | 5.7479 |  | 9.7479 | 4 | 9.7479 | 35.9242 | 17.9621 | 20 | 20 | -2.0379 | -85.9322
690 | 11.5 | 1.9825 | 10.344 | 2 | 10.4 | 35.9664 | 0 | 0.056047 | 111.6499 | 0.0013292 | 0.16814 | 5.5825 | 0.0039875 | 5.7546 |  | 9.7546 | 4 | 9.7546 | 35.9664 | 17.9832 | 20 | 20 | -2.0168 | -87.949
691 | 11.5167 | 1.9821 | 10.3426 | 2 | 10.4 | 36.0087 | 0 | 0.057363 | 111.7073 | 0.0013154 | 0.17209 | 5.5854 | 0.0039462 | 5.7614 |  | 9.7614 | 4 | 9.7614 | 36.0087 | 18.0044 | 20 | 20 | -1.9956 | -89.9446
692 | 11.5333 | 1.9817 | 10.3413 | 2 | 10.4 | 36.0512 | 0 | 0.058665 | 111.7659 | 0.0013016 | 0.17599 | 5.5883 | 0.0039048 | 5.7682 |  | 9.7682 | 4 | 9.7682 | 36.0512 | 18.0256 | 20 | 20 | -1.9744 | -91.919
693 | 11.55 | 1.9813 | 10.34 | 2 | 10.4 | 36.0938 | 0 | 0.059952 | 111.8259 | 0.0012878 | 0.17986 | 5.5913 | 0.0038633 | 5.775 |  | 9.775 | 4 | 9.775 | 36.0938 | 18.0469 | 20 | 20 | -1.9531 | -93.8721
694 | 11.5667 | 1.9809 | 10.3388 | 2 | 10.4 | 36.1366 | 0 | 0.061226 | 111.8871 | 0.0012739 | 0.18368 | 5.5944 | 0.0038216 | 5.7819 |  | 9.7819 | 4 | 9.7819 | 36.1366 | 18.0683 | 20 | 20 | -1.9317 | -95.8038
695 | 11.5833 | 1.9805 | 10.3375 | 2 | 10.4 | 36.1795 | 0 | 0.062486 | 111.9496 | 0.0012599 | 0.18746 | 5.5975 | 0.0037797 | 5.7887 |  | 9.7887 | 4 | 9.7887 | 36.1795 | 18.0897 | 20 | 20 | -1.9103 | -97.714
696 | 11.6 | 1.9801 | 10.3363 | 2 | 10.4 | 36.2225 | 0 | 0.063732 | 112.0133 | 0.0012459 | 0.1912 | 5.6007 | 0.0037378 | 5.7956 |  | 9.7956 | 4 | 9.7956 | 36.2225 | 18.1113 | 20 | 20 | -1.8887 | -99.6028
697 | 11.6167 | 1.9797 | 10.335 | 2 | 10.4 | 36.2656 | 0 | 0.064964 | 112.0783 | 0.0012319 | 0.19489 | 5.6039 | 0.0036957 | 5.8025 |  | 9.8025 | 4 | 9.8025 | 36.2656 | 18.1328 | 20 | 20 | -1.8672 | -101.4699
698 | 11.6333 | 1.9793 | 10.3338 | 2 | 10.4 | 36.3089 | 0 | 0.066182 | 112.1445 | 0.0012178 | 0.19855 | 5.6072 | 0.0036535 | 5.8094 |  | 9.8094 | 4 | 9.8094 | 36.3089 | 18.1544 | 20 | 20 | -1.8456 | -103.3155
699 | 11.65 | 1.9789 | 10.3326 | 2 | 10.4 | 36.3523 | 0 | 0.067385 | 112.2119 | 0.0012037 | 0.20216 | 5.6106 | 0.0036112 | 5.8164 |  | 9.8164 | 4 | 9.8164 | 36.3523 | 18.1761 | 20 | 20 | -1.8239 | -105.1394
700 | 11.6667 | 1.9786 | 10.3314 | 2 | 10.4 | 36.3957 | 0 | 0.068575 | 112.2805 | 0.0011896 | 0.20572 | 5.614 | 0.0035687 | 5.8233 |  | 9.8233 | 4 | 9.8233 | 36.3957 | 18.1979 | 20 | 20 | -1.8021 | -106.9415
701 | 11.6833 | 1.9782 | 10.3302 | 2 | 10.4 | 36.4393 | 0 | 0.06975 | 112.3502 | 0.0011754 | 0.20925 | 5.6175 | 0.0035262 | 5.8303 |  | 9.8303 | 4 | 9.8303 | 36.4393 | 18.2196 | 20 | 20 | -1.7804 | -108.7219
702 | 11.7 | 1.9778 | 10.3291 | 2 | 10.4 | 36.483 | 0 | 0.070912 | 112.4211 | 0.0011612 | 0.21273 | 5.6211 | 0.0034836 | 5.8373 |  | 9.8373 | 4 | 9.8373 | 36.483 | 18.2415 | 20 | 20 | -1.7585 | -110.4804
703 | 11.7167 | 1.9775 | 10.3279 | 2 | 10.4 | 36.5267 | 0 | 0.072059 | 112.4932 | 0.001147 | 0.21618 | 5.6247 | 0.0034409 | 5.8443 |  | 9.8443 | 4 | 9.8443 | 36.5267 | 18.2634 | 20 | 20 | -1.7366 | -112.217
704 | 11.7333 | 1.9771 | 10.3268 | 2 | 10.4 | 36.5706 | 0 | 0.073191 | 112.5664 | 0.0011327 | 0.21957 | 5.6283 | 0.0033981 | 5.8513 |  | 9.8513 | 4 | 9.8513 | 36.5706 | 18.2853 | 20 | 20 | -1.7147 | -113.9317
705 | 11.75 | 1.9768 | 10.3257 | 2 | 10.4 | 36.6145 | 0 | 0.07431 | 112.6407 | 0.0011184 | 0.22293 | 5.632 | 0.0033552 | 5.8583 |  | 9.8583 | 4 | 9.8583 | 36.6145 | 18.3072 | 20 | 20 | -1.6928 | -115.6245
706 | 11.7667 | 1.9764 | 10.3246 | 2 | 10.4 | 36.6585 | 0 | 0.075414 | 112.7161 | 0.0011041 | 0.22624 | 5.6358 | 0.0033122 | 5.8654 |  | 9.8654 | 4 | 9.8654 | 36.6585 | 18.3292 | 20 | 20 | -1.6708 | -117.2952
707 | 11.7833 | 1.9761 | 10.3235 | 2 | 10.4 | 36.7026 | 0 | 0.076503 | 112.7926 | 0.0010897 | 0.22951 | 5.6396 | 0.0032692 | 5.8724 |  | 9.8724 | 4 | 9.8724 | 36.7026 | 18.3513 | 20 | 20 | -1.6487 | -118.944
708 | 11.8 | 1.9758 | 10.3224 | 2 | 10.4 | 36.7467 | 0 | 0.077579 | 112.8702 | 0.0010753 | 0.23274 | 5.6435 | 0.003226 | 5.8795 |  | 9.8795 | 4 | 9.8795 | 36.7467 | 18.3733 | 20 | 20 | -1.6267 | -120.5706
709 | 11.8167 | 1.9754 | 10.3214 | 2 | 10.4 | 36.7909 | 0 | 0.07864 | 112.9488 | 0.001061 | 0.23592 | 5.6474 | 0.0031829 | 5.8865 |  | 9.8865 | 4 | 9.8865 | 36.7909 | 18.3954 | 20 | 20 | -1.6046 | -122.1752
710 | 11.8333 | 1.9751 | 10.3203 | 2 | 10.4 | 36.8351 | 0 | 0.079686 | 113.0285 | 0.0010465 | 0.23906 | 5.6514 | 0.0031396 | 5.8936 |  | 9.8936 | 4 | 9.8936 | 36.8351 | 18.4176 | 20 | 20 | -1.5824 | -123.7576
711 | 11.85 | 1.9748 | 10.3193 | 2 | 10.4 | 36.8794 | 0 | 0.080718 | 113.1092 | 0.0010321 | 0.24216 | 5.6555 | 0.0030963 | 5.9007 |  | 9.9007 | 4 | 9.9007 | 36.8794 | 18.4397 | 20 | 20 | -1.5603 | -125.3179
712 | 11.8667 | 1.9745 | 10.3183 | 2 | 10.4 | 36.9238 | 0 | 0.081736 | 113.1909 | 0.0010177 | 0.24521 | 5.6595 | 0.003053 | 5.9078 |  | 9.9078 | 4 | 9.9078 | 36.9238 | 18.4619 | 20 | 20 | -1.5381 | -126.856
713 | 11.8833 | 1.9741 | 10.3173 | 2 | 10.4 | 36.9682 | 0 | 0.082739 | 113.2737 | 0.0010032 | 0.24822 | 5.6637 | 0.0030096 | 5.9149 |  | 9.9149 | 4 | 9.9149 | 36.9682 | 18.4841 | 20 | 20 | -1.5159 | -128.3719
714 | 11.9 | 1.9738 | 10.3163 | 2 | 10.4 | 37.0126 | 0 | 0.083728 | 113.3574 | 0.00098872 | 0.25118 | 5.6679 | 0.0029661 | 5.922 |  | 9.922 | 4 | 9.922 | 37.0126 | 18.5063 | 20 | 20 | -1.4937 | -129.8656
715 | 11.9167 | 1.9735 | 10.3153 | 2 | 10.4 | 37.0571 | 0 | 0.084702 | 113.4421 | 0.00097423 | 0.25411 | 5.6721 | 0.0029227 | 5.9291 |  | 9.9291 | 4 | 9.9291 | 37.0571 | 18.5285 | 20 | 20 | -1.4715 | -131.337
716 | 11.9333 | 1.9732 | 10.3143 | 2 | 10.4 | 37.1016 | 0 | 0.085662 | 113.5278 | 0.00095972 | 0.25699 | 5.6764 | 0.0028792 | 5.9363 |  | 9.9363 | 4 | 9.9363 | 37.1016 | 18.5508 | 20 | 20 | -1.4492 | -132.7862
717 | 11.95 | 1.9729 | 10.3134 | 2 | 10.4 | 37.1461 | 0 | 0.086607 | 113.6144 | 0.00094522 | 0.25982 | 5.6807 | 0.0028356 | 5.9434 |  | 9.9434 | 4 | 9.9434 | 37.1461 | 18.5731 | 20 | 20 | -1.4269 | -134.2132
718 | 11.9667 | 1.9726 | 10.3125 | 2 | 10.4 | 37.1906 | 0 | 0.087538 | 113.7019 | 0.0009307 | 0.26261 | 5.6851 | 0.0027921 | 5.9505 |  | 9.9505 | 4 | 9.9505 | 37.1906 | 18.5953 | 20 | 20 | -1.4047 | -135.6179
719 | 11.9833 | 1.9724 | 10.3115 | 2 | 10.4 | 37.2352 | 0 | 0.088454 | 113.7904 | 0.00091618 | 0.26536 | 5.6895 | 0.0027485 | 5.9576 |  | 9.9576 | 4 | 9.9576 | 37.2352 | 18.6176 | 20 | 20 | -1.3824 | -137.0003
720 | 12 | 1.9721 | 10.3106 | 2 | 10.4 | 37.2797 | 0 | 0.089356 | 113.8797 | 0.00090165 | 0.26807 | 5.694 | 0.0027049 | 5.9648 |  | 9.9648 | 4 | 9.9648 | 37.2797 | 18.6399 | 20 | 20 | -1.3601 | -138.3604
721 | 12.0167 | 1.9718 | 10.3098 | 2 | 10.4 | 37.3243 | 0 | 0.090243 | 113.97 | 0.00088712 | 0.27073 | 5.6985 | 0.0026613 | 5.9719 |  | 9.9719 | 4 | 9.9719 | 37.3243 | 18.6622 | 20 | 20 | -1.3378 | -139.6982
722 | 12.0333 | 1.9715 | 10.3089 | 2 | 10.4 | 37.3689 | 0 | 0.091115 | 114.0611 | 0.00087258 | 0.27335 | 5.7031 | 0.0026178 | 5.979 |  | 9.979 | 4 | 9.979 | 37.3689 | 18.6844 | 20 | 20 | -1.3156 | -141.0138
723 | 12.05 | 1.9713 | 10.308 | 2 | 10.4 | 37.4134 | 0 | 0.091973 | 114.1531 | 0.00085805 | 0.27592 | 5.7077 | 0.0025742 | 5.9861 |  | 9.9861 | 4 | 9.9861 | 37.4134 | 18.7067 | 20 | 20 | -1.2933 | -142.3071
724 | 12.0667 | 1.971 | 10.3072 | 2 | 10.4 | 37.458 | 0 | 0.092817 | 114.2459 | 0.00084352 | 0.27845 | 5.7123 | 0.0025306 | 5.9933 |  | 9.9933 | 4 | 9.9933 | 37.458 | 18.729 | 20 | 20 | -1.271 | -143.5781
725 | 12.0833 | 1.9707 | 10.3064 | 2 | 10.4 | 37.5025 | 0 | 0.093646 | 114.3395 | 0.00082899 | 0.28094 | 5.717 | 0.002487 | 6.0004 |  | 10.0004 | 4 | 10.0004 | 37.5025 | 18.7513 | 20 | 20 | -1.2487 | -144.8269
726 | 12.1 | 1.9705 | 10.3055 | 2 | 10.4 | 37.547 | 0 | 0.09446 | 114.434 | 0.00081447 | 0.28338 | 5.7217 | 0.0024434 | 6.0075 |  | 10.0075 | 4 | 10.0075 | 37.547 | 18.7735 | 20 | 20 | -1.2265 | -146.0534
727 | 12.1167 | 1.9702 | 10.3047 | 2 | 10.4 | 37.5915 | 0 | 0.09526 | 114.5292 | 0.00079995 | 0.28578 | 5.7265 | 0.0023999 | 6.0146 |  | 10.0146 | 4 | 10.0146 | 37.5915 | 18.7958 | 20 | 20 | -1.2042 | -147.2576
728 | 12.1333 | 1.97 | 10.304 | 2 | 10.4 | 37.636 | 0 | 0.096046 | 114.6253 | 0.00078544 | 0.28814 | 5.7313 | 0.0023563 | 6.0218 |  | 10.0218 | 4 | 10.0218 | 37.636 | 18.818 | 20 | 20 | -1.182 | -148.4396
729 | 12.15 | 1.9697 | 10.3032 | 2 | 10.4 | 37.6804 | 0 | 0.096817 | 114.7221 | 0.00077094 | 0.29045 | 5.7361 | 0.0023128 | 6.0289 |  | 10.0289 | 4 | 10.0289 | 37.6804 | 18.8402 | 20 | 20 | -1.1598 | -149.5994
730 | 12.1667 | 1.9695 | 10.3024 | 2 | 10.4 | 37.7248 | 0 | 0.097573 | 114.8197 | 0.00075645 | 0.29272 | 5.741 | 0.0022693 | 6.036 |  | 10.036 | 4 | 10.036 | 37.7248 | 18.8624 | 20 | 20 | -1.1376 | -150.737
731 | 12.1833 | 1.9693 | 10.3017 | 2 | 10.4 | 37.7692 | 0 | 0.098315 | 114.918 | 0.00074197 | 0.29495 | 5.7459 | 0.0022259 | 6.0431 |  | 10.0431 | 4 | 10.0431 | 37.7692 | 18.8846 | 20 | 20 | -1.1154 | -151.8524
732 | 12.2 | 1.969 | 10.301 | 2 | 10.4 | 37.8135 | 0 | 0.099043 | 115.017 | 0.0007275 | 0.29713 | 5.7509 | 0.0021825 | 6.0502 |  | 10.0502 | 4 | 10.0502 | 37.8135 | 18.9068 | 20 | 20 | -1.0932 | -152.9456
733 | 12.2167 | 1.9688 | 10.3002 | 2 | 10.4 | 37.8578 | 0 | 0.099756 | 115.1168 | 0.00071304 | 0.29927 | 5.7558 | 0.0021391 | 6.0572 |  | 10.0572 | 4 | 10.0572 | 37.8578 | 18.9289 | 20 | 20 | -1.0711 | -154.0167
734 | 12.2333 | 1.9686 | 10.2995 | 2 | 10.4 | 37.902 | 0 | 0.10045 | 115.2173 | 0.00069861 | 0.30136 | 5.7609 | 0.0020958 | 6.0643 |  | 10.0643 | 4 | 10.0643 | 37.902 | 18.951 | 20 | 20 | -1.049 | -155.0657
735 | 12.25 | 1.9684 | 10.2989 | 2 | 10.4 | 37.9462 | 0 | 0.10114 | 115.3184 | 0.00068419 | 0.30342 | 5.7659 | 0.0020526 | 6.0714 |  | 10.0714 | 4 | 10.0714 | 37.9462 | 18.9731 | 20 | 20 | -1.0269 | -156.0926
736 | 12.2667 | 1.9682 | 10.2982 | 2 | 10.4 | 37.9903 | 0 | 0.10181 | 115.4202 | 0.00066978 | 0.30542 | 5.771 | 0.0020094 | 6.0784 |  | 10.0784 | 4 | 10.0784 | 37.9903 | 18.9951 | 20 | 20 | -1.0049 | -157.0975
737 | 12.2833 | 1.968 | 10.2975 | 2 | 10.4 | 38.0343 | 0 | 0.10246 | 115.5227 | 0.0006554 | 0.30739 | 5.7761 | 0.0019662 | 6.0855 |  | 10.0855 | 4 | 10.0855 | 38.0343 | 19.0172 | 20 | 20 | -0.98284 | -158.0803
738 | 12.3 | 1.9678 | 10.2969 | 2 | 10.4 | 38.0783 | 0 | 0.1031 | 115.6258 | 0.00064104 | 0.30931 | 5.7813 | 0.0019231 | 6.0925 |  | 10.0925 | 4 | 10.0925 | 38.0783 | 19.0391 | 20 | 20 | -0.96086 | -159.0412
739 | 12.3167 | 1.9676 | 10.2963 | 2 | 10.4 | 38.1222 | 0 | 0.10373 | 115.7295 | 0.0006267 | 0.31119 | 5.7865 | 0.0018801 | 6.0995 |  | 10.0995 | 4 | 10.0995 | 38.1222 | 19.0611 | 20 | 20 | -0.93891 | -159.9801
740 | 12.3333 | 1.9674 | 10.2957 | 2 | 10.4 | 38.166 | 0 | 0.10434 | 115.8338 | 0.00061238 | 0.31303 | 5.7917 | 0.0018372 | 6.1066 |  | 10.1066 | 4 | 10.1066 | 38.166 | 19.083 | 20 | 20 | -0.917 | -160.8971
741 | 12.35 | 1.9672 | 10.2951 | 2 | 10.4 | 38.2097 | 0 | 0.10494 | 115.9388 | 0.00059809 | 0.31483 | 5.7969 | 0.0017943 | 6.1136 |  | 10.1136 | 4 | 10.1136 | 38.2097 | 19.1049 | 20 | 20 | -0.89513 | -161.7922
742 | 12.3667 | 1.967 | 10.2945 | 2 | 10.4 | 38.2534 | 0 | 0.10553 | 116.0443 | 0.00058383 | 0.31658 | 5.8022 | 0.0017515 | 6.1205 |  | 10.1205 | 4 | 10.1205 | 38.2534 | 19.1267 | 20 | 20 | -0.8733 | -162.6655
743 | 12.3833 | 1.9668 | 10.2939 | 2 | 10.4 | 38.297 | 0 | 0.1061 | 116.1504 | 0.00056959 | 0.31829 | 5.8075 | 0.0017088 | 6.1275 |  | 10.1275 | 4 | 10.1275 | 38.297 | 19.1485 | 20 | 20 | -0.85152 | -163.5171
744 | 12.4 | 1.9667 | 10.2933 | 2 | 10.4 | 38.3404 | 0 | 0.10665 | 116.2571 | 0.00055538 | 0.31995 | 5.8129 | 0.0016662 | 6.1345 |  | 10.1345 | 4 | 10.1345 | 38.3404 | 19.1702 | 20 | 20 | -0.82978 | -164.3468
745 | 12.4167 | 1.9665 | 10.2928 | 2 | 10.4 | 38.3838 | 0 | 0.10719 | 116.3642 | 0.00054121 | 0.32158 | 5.8182 | 0.0016236 | 6.1414 |  | 10.1414 | 4 | 10.1414 | 38.3838 | 19.1919 | 20 | 20 | -0.80809 | -165.1549
746 | 12.4333 | 1.9663 | 10.2923 | 2 | 10.4 | 38.4271 | 0 | 0.10772 | 116.472 | 0.00052706 | 0.32316 | 5.8236 | 0.0015812 | 6.1483 |  | 10.1483 | 4 | 10.1483 | 38.4271 | 19.2136 | 20 | 20 | -0.78645 | -165.9414
747 | 12.45 | 1.9662 | 10.2918 | 2 | 10.4 | 38.4703 | 0 | 0.10823 | 116.5802 | 0.00051295 | 0.3247 | 5.829 | 0.0015388 | 6.1552 |  | 10.1552 | 4 | 10.1552 | 38.4703 | 19.2351 | 20 | 20 | -0.76486 | -166.7062
748 | 12.4667 | 1.966 | 10.2913 | 2 | 10.4 | 38.5133 | 0 | 0.10873 | 116.6889 | 0.00049887 | 0.32619 | 5.8344 | 0.0014966 | 6.1621 |  | 10.1621 | 4 | 10.1621 | 38.5133 | 19.2567 | 20 | 20 | -0.74333 | -167.4496
749 | 12.4833 | 1.9659 | 10.2908 | 2 | 10.4 | 38.5563 | 0 | 0.10922 | 116.7981 | 0.00048482 | 0.32765 | 5.8399 | 0.0014545 | 6.169 |  | 10.169 | 4 | 10.169 | 38.5563 | 19.2782 | 20 | 20 | -0.72185 | -168.1714
750 | 12.5 | 1.9657 | 10.2903 | 2 | 10.4 | 38.5991 | 0 | 0.10969 | 116.9078 | 0.00047081 | 0.32906 | 5.8454 | 0.0014124 | 6.1759 |  | 10.1759 | 4 | 10.1759 | 38.5991 | 19.2996 | 20 | 20 | -0.70043 | -168.8718
751 | 12.5167 | 1.9656 | 10.2899 | 2 | 10.4 | 38.6419 | 0 | 0.11014 | 117.018 | 0.00045684 | 0.33043 | 5.8509 | 0.0013705 | 6.1827 |  | 10.1827 | 4 | 10.1827 | 38.6419 | 19.3209 | 20 | 20 | -0.67907 | -169.5509
752 | 12.5333 | 1.9654 | 10.2894 | 2 | 10.4 | 38.6845 | 0 | 0.11059 | 117.1286 | 0.00044291 | 0.33176 | 5.8564 | 0.0013287 | 6.1895 |  | 10.1895 | 4 | 10.1895 | 38.6845 | 19.3422 | 20 | 20 | -0.65777 | -170.2087
753 | 12.55 | 1.9653 | 10.289 | 2 | 10.4 | 38.7269 | 0 | 0.11102 | 117.2396 | 0.00042901 | 0.33305 | 5.862 | 0.001287 | 6.1963 |  | 10.1963 | 4 | 10.1963 | 38.7269 | 19.3635 | 20 | 20 | -0.63653 | -170.8452
754 | 12.5667 | 1.9652 | 10.2886 | 2 | 10.4 | 38.7693 | 0 | 0.11143 | 117.351 | 0.00041516 | 0.33429 | 5.8676 | 0.0012455 | 6.2031 |  | 10.2031 | 4 | 10.2031 | 38.7693 | 19.3846 | 20 | 20 | -0.61535 | -171.4606
755 | 12.5833 | 1.9651 | 10.2882 | 2 | 10.4 | 38.8115 | 0 | 0.11183 | 117.4628 | 0.00040135 | 0.33549 | 5.8731 | 0.0012041 | 6.2098 |  | 10.2098 | 4 | 10.2098 | 38.8115 | 19.4058 | 20 | 20 | -0.59425 | -172.0548
756 | 12.6 | 1.9649 | 10.2878 | 2 | 10.4 | 38.8536 | 0 | 0.11222 | 117.5751 | 0.00038759 | 0.33666 | 5.8788 | 0.0011628 | 6.2166 |  | 10.2166 | 4 | 10.2166 | 38.8536 | 19.4268 | 20 | 20 | -0.57321 | -172.628
757 | 12.6167 | 1.9648 | 10.2874 | 2 | 10.4 | 38.8955 | 0 | 0.11259 | 117.6876 | 0.00037386 | 0.33778 | 5.8844 | 0.0011216 | 6.2233 |  | 10.2233 | 4 | 10.2233 | 38.8955 | 19.4478 | 20 | 20 | -0.55224 | -173.1803
758 | 12.6333 | 1.9647 | 10.287 | 2 | 10.4 | 38.9373 | 0 | 0.11295 | 117.8006 | 0.00036019 | 0.33886 | 5.89 | 0.0010806 | 6.23 |  | 10.23 | 4 | 10.23 | 38.9373 | 19.4687 | 20 | 20 | -0.53134 | -173.7116
759 | 12.65 | 1.9646 | 10.2867 | 2 | 10.4 | 38.979 | 0 | 0.1133 | 117.9139 | 0.00034656 | 0.3399 | 5.8957 | 0.0010397 | 6.2366 |  | 10.2366 | 4 | 10.2366 | 38.979 | 19.4895 | 20 | 20 | -0.51052 | -174.2221
760 | 12.6667 | 1.9645 | 10.2864 | 2 | 10.4 | 39.0205 | 0 | 0.11363 | 118.0275 | 0.00033298 | 0.3409 | 5.9014 | 0.00099893 | 6.2433 |  | 10.2433 | 4 | 10.2433 | 39.0205 | 19.5102 | 20 | 20 | -0.48977 | -174.7119
761 | 12.6833 | 1.9644 | 10.286 | 2 | 10.4 | 39.0618 | 0 | 0.11395 | 118.1415 | 0.00031944 | 0.34186 | 5.9071 | 0.00095832 | 6.2499 |  | 10.2499 | 4 | 10.2499 | 39.0618 | 19.5309 | 20 | 20 | -0.4691 | -175.181
762 | 12.7 | 1.9643 | 10.2857 | 2 | 10.4 | 39.103 | 0 | 0.11426 | 118.2557 | 0.00030596 | 0.34277 | 5.9128 | 0.00091787 | 6.2565 |  | 10.2565 | 4 | 10.2565 | 39.103 | 19.5515 | 20 | 20 | -0.4485 | -175.6295
763 | 12.7167 | 1.9642 | 10.2854 | 2 | 10.4 | 39.144 | 0 | 0.11455 | 118.3703 | 0.00029253 | 0.34365 | 5.9185 | 0.00087758 | 6.263 |  | 10.263 | 4 | 10.263 | 39.144 | 19.572 | 20 | 20 | -0.42799 | -176.0575
764 | 12.7333 | 1.9641 | 10.2852 | 2 | 10.4 | 39.1849 | 0 | 0.11483 | 118.4851 | 0.00027915 | 0.34449 | 5.9243 | 0.00083744 | 6.2696 |  | 10.2696 | 4 | 10.2696 | 39.1849 | 19.5924 | 20 | 20 | -0.40755 | -176.465
765 | 12.75 | 1.964 | 10.2849 | 2 | 10.4 | 39.2256 | 0 | 0.1151 | 118.6002 | 0.00026582 | 0.34529 | 5.93 | 0.00079745 | 6.2761 |  | 10.2761 | 4 | 10.2761 | 39.2256 | 19.6128 | 20 | 20 | -0.3872 | -176.8522
766 | 12.7667 | 1.964 | 10.2847 | 2 | 10.4 | 39.2661 | 0 | 0.11535 | 118.7156 | 0.00025254 | 0.34604 | 5.9358 | 0.00075763 | 6.2826 |  | 10.2826 | 4 | 10.2826 | 39.2661 | 19.6331 | 20 | 20 | -0.36694 | -177.2192
767 | 12.7833 | 1.9639 | 10.2844 | 2 | 10.4 | 39.3065 | 0 | 0.11559 | 118.8312 | 0.00023933 | 0.34676 | 5.9416 | 0.00071798 | 6.289 |  | 10.289 | 4 | 10.289 | 39.3065 | 19.6532 | 20 | 20 | -0.34676 | -177.5659
768 | 12.8 | 1.9638 | 10.2842 | 2 | 10.4 | 39.3467 | 0 | 0.11581 | 118.947 | 0.00022616 | 0.34744 | 5.9473 | 0.00067849 | 6.2955 |  | 10.2955 | 4 | 10.2955 | 39.3467 | 19.6733 | 20 | 20 | -0.32666 | -177.8926
769 | 12.8167 | 1.9637 | 10.284 | 2 | 10.4 | 39.3867 | 0 | 0.11603 | 119.063 | 0.00021306 | 0.34808 | 5.9531 | 0.00063918 | 6.3019 |  | 10.3019 | 4 | 10.3019 | 39.3867 | 19.6933 | 20 | 20 | -0.30666 | -178.1992
770 | 12.8333 | 1.9637 | 10.2838 | 2 | 10.4 | 39.4265 | 0 | 0.11623 | 119.1792 | 0.00020001 | 0.34868 | 5.959 | 0.00060004 | 6.3082 |  | 10.3082 | 4 | 10.3082 | 39.4265 | 19.7133 | 20 | 20 | -0.28675 | -178.486
771 | 12.85 | 1.9636 | 10.2836 | 2 | 10.4 | 39.4662 | 0 | 0.11641 | 119.2956 | 0.00018702 | 0.34924 | 5.9648 | 0.00056107 | 6.3146 |  | 10.3146 | 4 | 10.3146 | 39.4662 | 19.7331 | 20 | 20 | -0.26692 | -178.7529
772 | 12.8667 | 1.9636 | 10.2834 | 2 | 10.4 | 39.5056 | 0 | 0.11659 | 119.4122 | 0.0001741 | 0.34976 | 5.9706 | 0.00052229 | 6.3209 |  | 10.3209 | 4 | 10.3209 | 39.5056 | 19.7528 | 20 | 20 | -0.2472 | -179.0001
773 | 12.8833 | 1.9635 | 10.2833 | 2 | 10.4 | 39.5449 | 0 | 0.11675 | 119.529 | 0.00016123 | 0.35025 | 5.9764 | 0.00048369 | 6.3272 |  | 10.3272 | 4 | 10.3272 | 39.5449 | 19.7724 | 20 | 20 | -0.22756 | -179.2277
774 | 12.9 | 1.9635 | 10.2831 | 2 | 10.4 | 39.5839 | 0 | 0.1169 | 119.6459 | 0.00014842 | 0.35069 | 5.9823 | 0.00044527 | 6.3334 |  | 10.3334 | 4 | 10.3334 | 39.5839 | 19.792 | 20 | 20 | -0.20803 | -179.4357
775 | 12.9167 | 1.9634 | 10.283 | 2 | 10.4 | 39.6228 | 0 | 0.11703 | 119.7629 | 0.00013568 | 0.3511 | 5.9881 | 0.00040704 | 6.3397 |  | 10.3397 | 4 | 10.3397 | 39.6228 | 19.8114 | 20 | 20 | -0.18859 | -179.6243
776 | 12.9333 | 1.9634 | 10.2828 | 2 | 10.4 | 39.6615 | 0 | 0.11716 | 119.8801 | 0.000123 | 0.35147 | 5.994 | 0.00036901 | 6.3458 |  | 10.3458 | 4 | 10.3458 | 39.6615 | 19.8308 | 20 | 20 | -0.16925 | -179.7935
777 | 12.95 | 1.9634 | 10.2827 | 2 | 10.4 | 39.7 | 0 | 0.11727 | 119.9973 | 0.00011039 | 0.3518 | 5.9999 | 0.00033116 | 6.352 |  | 10.352 | 4 | 10.352 | 39.7 | 19.85 | 20 | 20 | -0.15001 | -179.9435
778 | 12.9667 | 1.9633 | 10.2826 | 2 | 10.4 | 39.7383 | 0 | 0.11736 | 120.1147 | 9.784e-05 | 0.35209 | 6.0057 | 0.00029352 | 6.3581 |  | 10.3581 | 4 | 10.3581 | 39.7383 | 19.8691 | 20 | 20 | -0.13087 | -180.0744
779 | 12.9833 | 1.9633 | 10.2826 | 2 | 10.4 | 39.7763 | 0 | 0.11745 | 120.2321 | 8.5358e-05 | 0.35235 | 6.0116 | 0.00025607 | 6.3642 |  | 10.3642 | 4 | 10.3642 | 39.7763 | 19.8882 | 20 | 20 | -0.11184 | -180.1862
780 | 13 | 1.9633 | 10.2825 | 2 | 10.4 | 39.8142 | 0 | 0.11752 | 120.3497 | 7.2942e-05 | 0.35257 | 6.0175 | 0.00021883 | 6.3703 |  | 10.3703 | 4 | 10.3703 | 39.8142 | 19.9071 | 20 | 20 | -0.092905 | -180.2791
781 | 13.0167 | 1.9633 | 10.2824 | 2 | 10.4 | 39.8518 | 0 | 0.11758 | 120.4672 | 6.0596e-05 | 0.35275 | 6.0234 | 0.00018179 | 6.3763 |  | 10.3763 | 4 | 10.3763 | 39.8518 | 19.9259 | 20 | 20 | -0.074081 | -180.3532
782 | 13.0333 | 1.9632 | 10.2824 | 2 | 10.4 | 39.8893 | 0 | 0.11763 | 120.5849 | 4.8318e-05 | 0.35289 | 6.0292 | 0.00014495 | 6.3823 |  | 10.3823 | 4 | 10.3823 | 39.8893 | 19.9446 | 20 | 20 | -0.055363 | -180.4086
783 | 13.05 | 1.9632 | 10.2823 | 2 | 10.4 | 39.9265 | 0 | 0.11767 | 120.7025 | 3.6109e-05 | 0.353 | 6.0351 | 0.00010833 | 6.3882 |  | 10.3882 | 4 | 10.3882 | 39.9265 | 19.9632 | 20 | 20 | -0.036753 | -180.4453
784 | 13.0667 | 1.9632 | 10.2823 | 2 | 10.4 | 39.9635 | 0 | 0.11769 | 120.8202 | 2.3971e-05 | 0.35308 | 6.041 | 7.1914e-05 | 6.3942 |  | 10.3942 | 4 | 10.3942 | 39.9635 | 19.9817 | 20 | 20 | -0.018253 | -180.4636
785 | 13.0833 | 1.9632 | 10.2823 | 2 | 10.4 | 40.0003 | 0 | 0.1177 | 120.9379 | 1.1905e-05 | 0.35311 | 6.0469 | 3.5715e-05 | 6.4 |  | 10.4 | 4 | 10.4 | 40.0003 | 20.0001 | 20 | 20 | 0.00013688 | -180.4635
786 | 13.1 | 1.9632 | 10.2823 | 2 | 10.4 | 40.0368 | 0 | 0.1177 | 121.0556 | -8.9276e-08 | 0.35311 | 6.0528 | -2.6783e-07 | 6.4059 |  | 10.4059 | 4 | 10.4059 | 40.0368 | 20.0184 | 20 | 20 | 0.018415 | -180.445
787 | 13.1167 | 1.9632 | 10.2823 | 2 | 10.4 | 40.0732 | 0 | 0.11769 | 121.1733 | -1.2011e-05 | 0.35307 | 6.0587 | -3.6032e-05 | 6.4117 |  | 10.4117 | 4 | 10.4117 | 40.0732 | 20.0366 | 20 | 20 | 0.03658 | -180.4085
788 | 13.1333 | 1.9632 | 10.2823 | 2 | 10.4 | 40.1093 | 0 | 0.11767 | 121.291 | -2.3858e-05 | 0.353 | 6.0646 | -7.1575e-05 | 6.4175 |  | 10.4175 | 4 | 10.4175 | 40.1093 | 20.0546 | 20 | 20 | 0.054631 | -180.3538
789 | 13.15 | 1.9632 | 10.2824 | 2 | 10.4 | 40.1451 | 0 | 0.11763 | 121.4086 | -3.5632e-05 | 0.3529 | 6.0704 | -0.00010689 | 6.4232 |  | 10.4232 | 4 | 10.4232 | 40.1451 | 20.0726 | 20 | 20 | 0.072566 | -180.2813
790 | 13.1667 | 1.9633 | 10.2824 | 2 | 10.4 | 40.1808 | 0 | 0.11758 | 121.5262 | -4.733e-05 | 0.35275 | 6.0763 | -0.00014199 | 6.4289 |  | 10.4289 | 4 | 10.4289 | 40.1808 | 20.0904 | 20 | 20 | 0.090385 | -180.1909
791 | 13.1833 | 1.9633 | 10.2825 | 2 | 10.4 | 40.2162 | 0 | 0.11753 | 121.6437 | -5.8952e-05 | 0.35258 | 6.0822 | -0.00017686 | 6.4346 |  | 10.4346 | 4 | 10.4346 | 40.2162 | 20.1081 | 20 | 20 | 0.10809 | -180.0828
792 | 13.2 | 1.9633 | 10.2825 | 2 | 10.4 | 40.2513 | 0 | 0.11746 | 121.7612 | -7.0498e-05 | 0.35237 | 6.0881 | -0.00021149 | 6.4402 |  | 10.4402 | 4 | 10.4402 | 40.2513 | 20.1257 | 20 | 20 | 0.12567 | -179.9571
793 | 13.2167 | 1.9633 | 10.2826 | 2 | 10.4 | 40.2863 | 0 | 0.11737 | 121.8786 | -8.1966e-05 | 0.35212 | 6.0939 | -0.0002459 | 6.4458 |  | 10.4458 | 4 | 10.4458 | 40.2863 | 20.1431 | 20 | 20 | 0.14313 | -179.814
794 | 13.2333 | 1.9634 | 10.2827 | 2 | 10.4 | 40.321 | 0 | 0.11728 | 121.9959 | -9.3356e-05 | 0.35184 | 6.0998 | -0.00028007 | 6.4514 |  | 10.4514 | 4 | 10.4514 | 40.321 | 20.1605 | 20 | 20 | 0.16048 | -179.6535
795 | 13.25 | 1.9634 | 10.2828 | 2 | 10.4 | 40.3554 | 0 | 0.11718 | 122.113 | -0.00010467 | 0.35153 | 6.1057 | -0.000314 | 6.4569 |  | 10.4569 | 4 | 10.4569 | 40.3554 | 20.1777 | 20 | 20 | 0.1777 | -179.4758
796 | 13.2667 | 1.9634 | 10.2829 | 2 | 10.4 | 40.3896 | 0 | 0.11706 | 122.2301 | -0.0001159 | 0.35118 | 6.1115 | -0.0003477 | 6.4623 |  | 10.4623 | 4 | 10.4623 | 40.3896 | 20.1948 | 20 | 20 | 0.1948 | -179.281
797 | 13.2833 | 1.9635 | 10.2831 | 2 | 10.4 | 40.4235 | 0 | 0.11693 | 122.347 | -0.00012705 | 0.3508 | 6.1174 | -0.00038116 | 6.4678 |  | 10.4678 | 4 | 10.4678 | 40.4235 | 20.2118 | 20 | 20 | 0.21177 | -179.0692
798 | 13.3 | 1.9635 | 10.2832 | 2 | 10.4 | 40.4572 | 0 | 0.11679 | 122.4638 | -0.00013812 | 0.35038 | 6.1232 | -0.00041437 | 6.4732 |  | 10.4732 | 4 | 10.4732 | 40.4572 | 20.2286 | 20 | 20 | 0.22862 | -178.8406
799 | 13.3167 | 1.9635 | 10.2834 | 2 | 10.4 | 40.4907 | 0 | 0.11665 | 122.5805 | -0.00014911 | 0.34994 | 6.129 | -0.00044734 | 6.4785 |  | 10.4785 | 4 | 10.4785 | 40.4907 | 20.2453 | 20 | 20 | 0.24535 | -178.5953
800 | 13.3333 | 1.9636 | 10.2835 | 2 | 10.4 | 40.5239 | 0 | 0.11649 | 122.6969 | -0.00016002 | 0.34946 | 6.1348 | -0.00048007 | 6.4838 |  | 10.4838 | 4 | 10.4838 | 40.5239 | 20.2619 | 20 | 20 | 0.26195 | -178.3333
801 | 13.35 | 1.9637 | 10.2837 | 2 | 10.4 | 40.5568 | 0 | 0.11631 | 122.8133 | -0.00017085 | 0.34894 | 6.1407 | -0.00051255 | 6.4891 |  | 10.4891 | 4 | 10.4891 | 40.5568 | 20.2784 | 20 | 20 | 0.27842 | -178.0549
802 | 13.3667 | 1.9637 | 10.2839 | 2 | 10.4 | 40.5895 | 0 | 0.11613 | 122.9294 | -0.00018159 | 0.3484 | 6.1465 | -0.00054477 | 6.4943 |  | 10.4943 | 4 | 10.4943 | 40.5895 | 20.2948 | 20 | 20 | 0.29476 | -177.7601
803 | 13.3833 | 1.9638 | 10.2841 | 2 | 10.4 | 40.6219 | 0 | 0.11594 | 123.0453 | -0.00019225 | 0.34782 | 6.1523 | -0.00057675 | 6.4995 |  | 10.4995 | 4 | 10.4995 | 40.6219 | 20.311 | 20 | 20 | 0.31097 | -177.4492
804 | 13.4 | 1.9638 | 10.2843 | 2 | 10.4 | 40.6541 | 0 | 0.11574 | 123.1611 | -0.00020283 | 0.34721 | 6.1581 | -0.00060848 | 6.5047 |  | 10.5047 | 4 | 10.5047 | 40.6541 | 20.3271 | 20 | 20 | 0.32706 | -177.1221
805 | 13.4167 | 1.9639 | 10.2845 | 2 | 10.4 | 40.686 | 0 | 0.11552 | 123.2766 | -0.00021332 | 0.34657 | 6.1638 | -0.00063995 | 6.5098 |  | 10.5098 | 4 | 10.5098 | 40.686 | 20.343 | 20 | 20 | 0.34301 | -176.7791
806 | 13.4333 | 1.964 | 10.2847 | 2 | 10.4 | 40.7177 | 0 | 0.1153 | 123.3919 | -0.00022372 | 0.3459 | 6.1696 | -0.00067116 | 6.5148 |  | 10.5148 | 4 | 10.5148 | 40.7177 | 20.3588 | 20 | 20 | 0.35883 | -176.4203
807 | 13.45 | 1.964 | 10.2849 | 2 | 10.4 | 40.749 | 0 | 0.11507 | 123.507 | -0.00023404 | 0.3452 | 6.1753 | -0.00070212 | 6.5198 |  | 10.5198 | 4 | 10.5198 | 40.749 | 20.3745 | 20 | 20 | 0.37452 | -176.0458
808 | 13.4667 | 1.9641 | 10.2852 | 2 | 10.4 | 40.7801 | 0 | 0.11482 | 123.6218 | -0.00024427 | 0.34447 | 6.1811 | -0.00073281 | 6.5248 |  | 10.5248 | 4 | 10.5248 | 40.7801 | 20.3901 | 20 | 20 | 0.39007 | -175.6557
809 | 13.4833 | 1.9642 | 10.2854 | 2 | 10.4 | 40.811 | 0 | 0.11457 | 123.7364 | -0.00025442 | 0.3437 | 6.1868 | -0.00076325 | 6.5298 |  | 10.5298 | 4 | 10.5298 | 40.811 | 20.4055 | 20 | 20 | 0.40549 | -175.2502
810 | 13.5 | 1.9643 | 10.2857 | 2 | 10.4 | 40.8416 | 0 | 0.1143 | 123.8507 | -0.00026447 | 0.34291 | 6.1925 | -0.00079342 | 6.5346 |  | 10.5346 | 4 | 10.5346 | 40.8416 | 20.4208 | 20 | 20 | 0.42078 | -174.8294
811 | 13.5167 | 1.9644 | 10.286 | 2 | 10.4 | 40.8719 | 0 | 0.11403 | 123.9647 | -0.00027444 | 0.34209 | 6.1982 | -0.00082333 | 6.5395 |  | 10.5395 | 4 | 10.5395 | 40.8719 | 20.4359 | 20 | 20 | 0.43593 | -174.3935
812 | 13.5333 | 1.9645 | 10.2863 | 2 | 10.4 | 40.9019 | 0 | 0.11374 | 124.0784 | -0.00028433 | 0.34123 | 6.2039 | -0.00085298 | 6.5443 |  | 10.5443 | 4 | 10.5443 | 40.9019 | 20.4509 | 20 | 20 | 0.45094 | -173.9425
813 | 13.55 | 1.9645 | 10.2865 | 2 | 10.4 | 40.9316 | 0 | 0.11345 | 124.1919 | -0.00029412 | 0.34035 | 6.2096 | -0.00088236 | 6.5491 |  | 10.5491 | 4 | 10.5491 | 40.9316 | 20.4658 | 20 | 20 | 0.46582 | -173.4767
814 | 13.5667 | 1.9646 | 10.2869 | 2 | 10.4 | 40.9611 | 0 | 0.11315 | 124.305 | -0.00030382 | 0.33944 | 6.2153 | -0.00091147 | 6.5538 |  | 10.5538 | 4 | 10.5538 | 40.9611 | 20.4806 | 20 | 20 | 0.48056 | -172.9962
815 | 13.5833 | 1.9647 | 10.2872 | 2 | 10.4 | 40.9903 | 0 | 0.11283 | 124.4179 | -0.00031344 | 0.3385 | 6.2209 | -0.00094031 | 6.5585 |  | 10.5585 | 4 | 10.5585 | 40.9903 | 20.4952 | 20 | 20 | 0.49516 | -172.501
816 | 13.6 | 1.9648 | 10.2875 | 2 | 10.4 | 41.0193 | 0 | 0.11251 | 124.5304 | -0.00032296 | 0.33753 | 6.2265 | -0.00096888 | 6.5631 |  | 10.5631 | 4 | 10.5631 | 41.0193 | 20.5096 | 20 | 20 | 0.50963 | -171.9914
817 | 13.6167 | 1.9649 | 10.2878 | 2 | 10.4 | 41.0479 | 0 | 0.11218 | 124.6425 | -0.00033239 | 0.33653 | 6.2321 | -0.00099718 | 6.5677 |  | 10.5677 | 4 | 10.5677 | 41.0479 | 20.5239 | 20 | 20 | 0.52395 | -171.4674
818 | 13.6333 | 1.9651 | 10.2882 | 2 | 10.4 | 41.0763 | 0 | 0.11184 | 124.7544 | -0.00034173 | 0.33551 | 6.2377 | -0.0010252 | 6.5722 |  | 10.5722 | 4 | 10.5722 | 41.0763 | 20.5381 | 20 | 20 | 0.53813 | -170.9293
819 | 13.65 | 1.9652 | 10.2885 | 2 | 10.4 | 41.1043 | 0 | 0.11149 | 124.8659 | -0.00035099 | 0.33446 | 6.2433 | -0.001053 | 6.5767 |  | 10.5767 | 4 | 10.5767 | 41.1043 | 20.5522 | 20 | 20 | 0.55217 | -170.3771
820 | 13.6667 | 1.9653 | 10.2889 | 2 | 10.4 | 41.1322 | 0 | 0.11112 | 124.977 | -0.00036014 | 0.33337 | 6.2488 | -0.0010804 | 6.5811 |  | 10.5811 | 4 | 10.5811 | 41.1322 | 20.5661 | 20 | 20 | 0.56608 | -169.811
821 | 13.6833 | 1.9654 | 10.2892 | 2 | 10.4 | 41.1597 | 0 | 0.11076 | 125.0878 | -0.00036921 | 0.33227 | 6.2544 | -0.0011076 | 6.5855 |  | 10.5855 | 4 | 10.5855 | 41.1597 | 20.5798 | 20 | 20 | 0.57983 | -169.2312
822 | 13.7 | 1.9655 | 10.2896 | 2 | 10.4 | 41.1869 | 0 | 0.11038 | 125.1981 | -0.00037819 | 0.33113 | 6.2599 | -0.0011346 | 6.5899 |  | 10.5899 | 4 | 10.5899 | 41.1869 | 20.5935 | 20 | 20 | 0.59345 | -168.6378
823 | 13.7167 | 1.9656 | 10.29 | 2 | 10.4 | 41.2139 | 0 | 0.10999 | 125.3081 | -0.00038707 | 0.32997 | 6.2654 | -0.0011612 | 6.5942 |  | 10.5942 | 4 | 10.5942 | 41.2139 | 20.6069 | 20 | 20 | 0.60693 | -168.0308
824 | 13.7333 | 1.9658 | 10.2904 | 2 | 10.4 | 41.2405 | 0 | 0.10959 | 125.4177 | -0.00039585 | 0.32878 | 6.2709 | -0.0011876 | 6.5985 |  | 10.5985 | 4 | 10.5985 | 41.2405 | 20.6203 | 20 | 20 | 0.62026 | -167.4106
825 | 13.75 | 1.9659 | 10.2908 | 2 | 10.4 | 41.2669 | 0 | 0.10919 | 125.5269 | -0.00040455 | 0.32757 | 6.2763 | -0.0012136 | 6.6027 |  | 10.6027 | 4 | 10.6027 | 41.2669 | 20.6334 | 20 | 20 | 0.63344 | -166.7771
826 | 13.7667 | 1.966 | 10.2912 | 2 | 10.4 | 41.293 | 0 | 0.10878 | 125.6357 | -0.00041315 | 0.32633 | 6.2818 | -0.0012395 | 6.6069 |  | 10.6069 | 4 | 10.6069 | 41.293 | 20.6465 | 20 | 20 | 0.64649 | -166.1306
827 | 13.7833 | 1.9661 | 10.2916 | 2 | 10.4 | 41.3188 | 0 | 0.10836 | 125.744 | -0.00042166 | 0.32507 | 6.2872 | -0.001265 | 6.611 |  | 10.611 | 4 | 10.611 | 41.3188 | 20.6594 | 20 | 20 | 0.65938 | -165.4713
828 | 13.8 | 1.9663 | 10.2921 | 2 | 10.4 | 41.3443 | 0 | 0.10793 | 125.852 | -0.00043007 | 0.32378 | 6.2926 | -0.0012902 | 6.6151 |  | 10.6151 | 4 | 10.6151 | 41.3443 | 20.6721 | 20 | 20 | 0.67214 | -164.7991
829 | 13.8167 | 1.9664 | 10.2925 | 2 | 10.4 | 41.3695 | 0 | 0.10749 | 125.9594 | -0.00043839 | 0.32246 | 6.298 | -0.0013152 | 6.6191 |  | 10.6191 | 4 | 10.6191 | 41.3695 | 20.6847 | 20 | 20 | 0.68474 | -164.1144
830 | 13.8333 | 1.9665 | 10.293 | 2 | 10.4 | 41.3944 | 0 | 0.10704 | 126.0665 | -0.00044661 | 0.32112 | 6.3033 | -0.0013398 | 6.6231 |  | 10.6231 | 4 | 10.6231 | 41.3944 | 20.6972 | 20 | 20 | 0.6972 | -163.4172
831 | 13.85 | 1.9667 | 10.2934 | 2 | 10.4 | 41.419 | 0 | 0.10659 | 126.1731 | -0.00045474 | 0.31976 | 6.3087 | -0.0013642 | 6.627 |  | 10.627 | 4 | 10.627 | 41.419 | 20.7095 | 20 | 20 | 0.70952 | -162.7077
832 | 13.8667 | 1.9668 | 10.2939 | 2 | 10.4 | 41.4434 | 0 | 0.10612 | 126.2792 | -0.00046277 | 0.31837 | 6.314 | -0.0013883 | 6.6309 |  | 10.6309 | 4 | 10.6309 | 41.4434 | 20.7217 | 20 | 20 | 0.72169 | -161.986
833 | 13.8833 | 1.967 | 10.2943 | 2 | 10.4 | 41.4674 | 0 | 0.10565 | 126.3848 | -0.0004707 | 0.31696 | 6.3192 | -0.0014121 | 6.6348 |  | 10.6348 | 4 | 10.6348 | 41.4674 | 20.7337 | 20 | 20 | 0.73371 | -161.2523
834 | 13.9 | 1.9671 | 10.2948 | 2 | 10.4 | 41.4912 | 0 | 0.10517 | 126.49 | -0.00047855 | 0.31552 | 6.3245 | -0.0014356 | 6.6386 |  | 10.6386 | 4 | 10.6386 | 41.4912 | 20.7456 | 20 | 20 | 0.74558 | -160.5067
835 | 13.9167 | 1.9673 | 10.2953 | 2 | 10.4 | 41.5146 | 0 | 0.10469 | 126.5947 | -0.00048629 | 0.31406 | 6.3297 | -0.0014589 | 6.6423 |  | 10.6423 | 4 | 10.6423 | 41.5146 | 20.7573 | 20 | 20 | 0.75731 | -159.7494
836 | 13.9333 | 1.9674 | 10.2958 | 2 | 10.4 | 41.5378 | 0 | 0.10419 | 126.6989 | -0.00049394 | 0.31258 | 6.3349 | -0.0014818 | 6.646 |  | 10.646 | 4 | 10.646 | 41.5378 | 20.7689 | 20 | 20 | 0.76888 | -158.9805
837 | 13.95 | 1.9676 | 10.2963 | 2 | 10.4 | 41.5606 | 0 | 0.10369 | 126.8026 | -0.00050149 | 0.31108 | 6.3401 | -0.0015045 | 6.6497 |  | 10.6497 | 4 | 10.6497 | 41.5606 | 20.7803 | 20 | 20 | 0.78031 | -158.2002
838 | 13.9667 | 1.9678 | 10.2968 | 2 | 10.4 | 41.5832 | 0 | 0.10318 | 126.9058 | -0.00050894 | 0.30955 | 6.3453 | -0.0015268 | 6.6533 |  | 10.6533 | 4 | 10.6533 | 41.5832 | 20.7916 | 20 | 20 | 0.7916 | -157.4086
839 | 13.9833 | 1.9679 | 10.2973 | 2 | 10.4 | 41.6055 | 0 | 0.10267 | 127.0084 | -0.0005163 | 0.308 | 6.3504 | -0.0015489 | 6.6569 |  | 10.6569 | 4 | 10.6569 | 41.6055 | 20.8027 | 20 | 20 | 0.80273 | -156.6059
840 | 14 | 1.9681 | 10.2979 | 2 | 10.4 | 41.6274 | 0 | 0.10214 | 127.1106 | -0.00052356 | 0.30643 | 6.3555 | -0.0015707 | 6.6604 |  | 10.6604 | 4 | 10.6604 | 41.6274 | 20.8137 | 20 | 20 | 0.81371 | -155.7921
841 | 14.0167 | 1.9682 | 10.2984 | 2 | 10.4 | 41.6491 | 0 | 0.10161 | 127.2122 | -0.00053073 | 0.30484 | 6.3606 | -0.0015922 | 6.6639 |  | 10.6639 | 4 | 10.6639 | 41.6491 | 20.8245 | 20 | 20 | 0.82454 | -154.9676
842 | 14.0333 | 1.9684 | 10.2989 | 2 | 10.4 | 41.6705 | 0 | 0.10107 | 127.3133 | -0.00053779 | 0.30322 | 6.3657 | -0.0016134 | 6.6673 |  | 10.6673 | 4 | 10.6673 | 41.6705 | 20.8352 | 20 | 20 | 0.83523 | -154.1324
843 | 14.05 | 1.9686 | 10.2995 | 2 | 10.4 | 41.6915 | 0 | 0.10053 | 127.4138 | -0.00054476 | 0.30159 | 6.3707 | -0.0016343 | 6.6706 |  | 10.6706 | 4 | 10.6706 | 41.6915 | 20.8458 | 20 | 20 | 0.84577 | -153.2866
844 | 14.0667 | 1.9688 | 10.3 | 2 | 10.4 | 41.7123 | 0 | 0.099978 | 127.5138 | -0.00055163 | 0.29993 | 6.3757 | -0.0016549 | 6.674 |  | 10.674 | 4 | 10.674 | 41.7123 | 20.8562 | 20 | 20 | 0.85615 | -152.4305
845 | 14.0833 | 1.9689 | 10.3006 | 2 | 10.4 | 41.7328 | 0 | 0.09942 | 127.6132 | -0.00055841 | 0.29826 | 6.3807 | -0.0016752 | 6.6772 |  | 10.6772 | 4 | 10.6772 | 41.7328 | 20.8664 | 20 | 20 | 0.86639 | -151.5641
846 | 14.1 | 1.9691 | 10.3011 | 2 | 10.4 | 41.7529 | 0 | 0.098855 | 127.7121 | -0.00056508 | 0.29656 | 6.3856 | -0.0016952 | 6.6805 |  | 10.6805 | 4 | 10.6805 | 41.7529 | 20.8765 | 20 | 20 | 0.87647 | -150.6876
847 | 14.1167 | 1.9693 | 10.3017 | 2 | 10.4 | 41.7728 | 0 | 0.098283 | 127.8103 | -0.00057166 | 0.29485 | 6.3905 | -0.001715 | 6.6837 |  | 10.6837 | 4 | 10.6837 | 41.7728 | 20.8864 | 20 | 20 | 0.88641 | -149.8012
848 | 14.1333 | 1.9695 | 10.3023 | 2 | 10.4 | 41.7924 | 0 | 0.097705 | 127.908 | -0.00057814 | 0.29311 | 6.3954 | -0.0017344 | 6.6868 |  | 10.6868 | 4 | 10.6868 | 41.7924 | 20.8962 | 20 | 20 | 0.89619 | -148.905
849 | 14.15 | 1.9696 | 10.3029 | 2 | 10.4 | 41.8117 | 0 | 0.09712 | 128.0052 | -0.00058452 | 0.29136 | 6.4003 | -0.0017536 | 6.6899 |  | 10.6899 | 4 | 10.6899 | 41.8117 | 20.9058 | 20 | 20 | 0.90583 | -147.9992
850 | 14.1667 | 1.9698 | 10.3035 | 2 | 10.4 | 41.8306 | 0 | 0.096529 | 128.1017 | -0.00059081 | 0.28959 | 6.4051 | -0.0017724 | 6.6929 |  | 10.6929 | 4 | 10.6929 | 41.8306 | 20.9153 | 20 | 20 | 0.91531 | -147.0839
851 | 14.1833 | 1.97 | 10.3041 | 2 | 10.4 | 41.8493 | 0 | 0.095932 | 128.1976 | -0.00059699 | 0.2878 | 6.4099 | -0.001791 | 6.6959 |  | 10.6959 | 4 | 10.6959 | 41.8493 | 20.9246 | 20 | 20 | 0.92465 | -146.1592
852 | 14.2 | 1.9702 | 10.3047 | 2 | 10.4 | 41.8677 | 0 | 0.095329 | 128.293 | -0.00060308 | 0.28599 | 6.4146 | -0.0018092 | 6.6988 |  | 10.6988 | 4 | 10.6988 | 41.8677 | 20.9338 | 20 | 20 | 0.93383 | -145.2254
853 | 14.2167 | 1.9704 | 10.3053 | 2 | 10.4 | 41.8857 | 0 | 0.09472 | 128.3877 | -0.00060907 | 0.28416 | 6.4194 | -0.0018272 | 6.7017 |  | 10.7017 | 4 | 10.7017 | 41.8857 | 20.9429 | 20 | 20 | 0.94287 | -144.2825
854 | 14.2333 | 1.9706 | 10.3059 | 2 | 10.4 | 41.9035 | 0 | 0.094105 | 128.4818 | -0.00061497 | 0.28232 | 6.4241 | -0.0018449 | 6.7046 |  | 10.7046 | 4 | 10.7046 | 41.9035 | 20.9517 | 20 | 20 | 0.95175 | -143.3308
855 | 14.25 | 1.9708 | 10.3065 | 2 | 10.4 | 41.921 | 0 | 0.093485 | 128.5753 | -0.00062076 | 0.28045 | 6.4288 | -0.0018623 | 6.7074 |  | 10.7074 | 4 | 10.7074 | 41.921 | 20.9605 | 20 | 20 | 0.96048 | -142.3703
856 | 14.2667 | 1.971 | 10.3071 | 2 | 10.4 | 41.9381 | 0 | 0.092858 | 128.6681 | -0.00062645 | 0.27857 | 6.4334 | -0.0018794 | 6.7101 |  | 10.7101 | 4 | 10.7101 | 41.9381 | 20.9691 | 20 | 20 | 0.96907 | -141.4012
857 | 14.2833 | 1.9712 | 10.3078 | 2 | 10.4 | 41.955 | 0 | 0.092226 | 128.7603 | -0.00063205 | 0.27668 | 6.438 | -0.0018962 | 6.7128 |  | 10.7128 | 4 | 10.7128 | 41.955 | 20.9775 | 20 | 20 | 0.9775 | -140.4237
858 | 14.3 | 1.9714 | 10.3084 | 2 | 10.4 | 41.9716 | 0 | 0.091588 | 128.8519 | -0.00063755 | 0.27477 | 6.4426 | -0.0019127 | 6.7154 |  | 10.7154 | 4 | 10.7154 | 41.9716 | 20.9858 | 20 | 20 | 0.98578 | -139.4379
859 | 14.3167 | 1.9716 | 10.3091 | 2 | 10.4 | 41.9878 | 0 | 0.090946 | 128.9429 | -0.00064295 | 0.27284 | 6.4471 | -0.0019289 | 6.7181 |  | 10.7181 | 4 | 10.7181 | 41.9878 | 20.9939 | 20 | 20 | 0.99391 | -138.444
860 | 14.3333 | 1.9718 | 10.3097 | 2 | 10.4 | 42.0038 | 0 | 0.090297 | 129.0332 | -0.00064826 | 0.27089 | 6.4517 | -0.0019448 | 6.7206 |  | 10.7206 | 4 | 10.7206 | 42.0038 | 21.0019 | 20 | 20 | 1.0019 | -137.4421
861 | 14.35 | 1.972 | 10.3104 | 2 | 10.4 | 42.0195 | 0 | 0.089644 | 129.1228 | -0.00065346 | 0.26893 | 6.4561 | -0.0019604 | 6.7231 |  | 10.7231 | 4 | 10.7231 | 42.0195 | 21.0097 | 20 | 20 | 1.0097 | -136.4324
862 | 14.3667 | 1.9722 | 10.311 | 2 | 10.4 | 42.0348 | 0 | 0.088985 | 129.2118 | -0.00065857 | 0.26696 | 6.4606 | -0.0019757 | 6.7256 |  | 10.7256 | 4 | 10.7256 | 42.0348 | 21.0174 | 20 | 20 | 1.0174 | -135.415
863 | 14.3833 | 1.9724 | 10.3117 | 2 | 10.4 | 42.0499 | 0 | 0.088322 | 129.3001 | -0.00066358 | 0.26496 | 6.465 | -0.0019907 | 6.728 |  | 10.728 | 4 | 10.728 | 42.0499 | 21.0249 | 20 | 20 | 1.0249 | -134.3901
864 | 14.4 | 1.9726 | 10.3123 | 2 | 10.4 | 42.0646 | 0 | 0.087653 | 129.3878 | -0.0006685 | 0.26296 | 6.4694 | -0.0020055 | 6.7303 |  | 10.7303 | 4 | 10.7303 | 42.0646 | 21.0323 | 20 | 20 | 1.0323 | -133.3577
865 | 14.4167 | 1.9728 | 10.313 | 2 | 10.4 | 42.0791 | 0 | 0.08698 | 129.4748 | -0.00067331 | 0.26094 | 6.4737 | -0.0020199 | 6.7327 |  | 10.7327 | 4 | 10.7327 | 42.0791 | 21.0396 | 20 | 20 | 1.0396 | -132.3182
866 | 14.4333 | 1.973 | 10.3137 | 2 | 10.4 | 42.0933 | 0 | 0.086302 | 129.5611 | -0.00067803 | 0.25891 | 6.4781 | -0.0020341 | 6.7349 |  | 10.7349 | 4 | 10.7349 | 42.0933 | 21.0466 | 20 | 20 | 1.0466 | -131.2715
867 | 14.45 | 1.9732 | 10.3144 | 2 | 10.4 | 42.1071 | 0 | 0.085619 | 129.6467 | -0.00068265 | 0.25686 | 6.4823 | -0.0020479 | 6.7371 |  | 10.7371 | 4 | 10.7371 | 42.1071 | 21.0536 | 20 | 20 | 1.0536 | -130.218
868 | 14.4667 | 1.9735 | 10.3151 | 2 | 10.4 | 42.1207 | 0 | 0.084932 | 129.7316 | -0.00068717 | 0.2548 | 6.4866 | -0.0020615 | 6.7393 |  | 10.7393 | 4 | 10.7393 | 42.1207 | 21.0604 | 20 | 20 | 1.0604 | -129.1576
869 | 14.4833 | 1.9737 | 10.3158 | 2 | 10.4 | 42.134 | 0 | 0.08424 | 129.8159 | -0.0006916 | 0.25272 | 6.4908 | -0.0020748 | 6.7414 |  | 10.7414 | 4 | 10.7414 | 42.134 | 21.067 | 20 | 20 | 1.067 | -128.0906
870 | 14.5 | 1.9739 | 10.3165 | 2 | 10.4 | 42.147 | 0 | 0.083544 | 129.8994 | -0.00069593 | 0.25063 | 6.495 | -0.0020878 | 6.7435 |  | 10.7435 | 4 | 10.7435 | 42.147 | 21.0735 | 20 | 20 | 1.0735 | -127.0171
871 | 14.5167 | 1.9741 | 10.3172 | 2 | 10.4 | 42.1597 | 0 | 0.082844 | 129.9822 | -0.00070016 | 0.24853 | 6.4991 | -0.0021005 | 6.7455 |  | 10.7455 | 4 | 10.7455 | 42.1597 | 21.0798 | 20 | 20 | 1.0798 | -125.9373
872 | 14.5333 | 1.9743 | 10.3179 | 2 | 10.4 | 42.172 | 0 | 0.08214 | 130.0644 | -0.00070429 | 0.24642 | 6.5032 | -0.0021129 | 6.7475 |  | 10.7475 | 4 | 10.7475 | 42.172 | 21.086 | 20 | 20 | 1.086 | -124.8513
873 | 14.55 | 1.9746 | 10.3186 | 2 | 10.4 | 42.1841 | 0 | 0.081432 | 130.1458 | -0.00070833 | 0.24429 | 6.5073 | -0.002125 | 6.7495 |  | 10.7495 | 4 | 10.7495 | 42.1841 | 21.0921 | 20 | 20 | 1.0921 | -123.7592
874 | 14.5667 | 1.9748 | 10.3193 | 2 | 10.4 | 42.1959 | 0 | 0.080719 | 130.2265 | -0.00071228 | 0.24216 | 6.5113 | -0.0021368 | 6.7513 |  | 10.7513 | 4 | 10.7513 | 42.1959 | 21.098 | 20 | 20 | 1.098 | -122.6612
875 | 14.5833 | 1.975 | 10.32 | 2 | 10.4 | 42.2074 | 0 | 0.080003 | 130.3065 | -0.00071612 | 0.24001 | 6.5153 | -0.0021484 | 6.7532 |  | 10.7532 | 4 | 10.7532 | 42.2074 | 21.1037 | 20 | 20 | 1.1037 | -121.5575
876 | 14.6 | 1.9752 | 10.3207 | 2 | 10.4 | 42.2186 | 0 | 0.079283 | 130.3858 | -0.00071987 | 0.23785 | 6.5193 | -0.0021596 | 6.755 |  | 10.755 | 4 | 10.755 | 42.2186 | 21.1093 | 20 | 20 | 1.1093 | -120.4482
877 | 14.6167 | 1.9755 | 10.3214 | 2 | 10.4 | 42.2296 | 0 | 0.07856 | 130.4644 | -0.00072353 | 0.23568 | 6.5232 | -0.0021706 | 6.7567 |  | 10.7567 | 4 | 10.7567 | 42.2296 | 21.1148 | 20 | 20 | 1.1148 | -119.3334
878 | 14.6333 | 1.9757 | 10.3222 | 2 | 10.4 | 42.2402 | 0 | 0.077833 | 130.5422 | -0.00072709 | 0.2335 | 6.5271 | -0.0021813 | 6.7584 |  | 10.7584 | 4 | 10.7584 | 42.2402 | 21.1201 | 20 | 20 | 1.1201 | -118.2134
879 | 14.65 | 1.9759 | 10.3229 | 2 | 10.4 | 42.2505 | 0 | 0.077102 | 130.6193 | -0.00073055 | 0.23131 | 6.531 | -0.0021917 | 6.7601 |  | 10.7601 | 4 | 10.7601 | 42.2505 | 21.1253 | 20 | 20 | 1.1253 | -117.0881
880 | 14.6667 | 1.9761 | 10.3236 | 2 | 10.4 | 42.2605 | 0 | 0.076368 | 130.6957 | -0.00073392 | 0.2291 | 6.5348 | -0.0022018 | 6.7617 |  | 10.7617 | 4 | 10.7617 | 42.2605 | 21.1303 | 20 | 20 | 1.1303 | -115.9578
881 | 14.6833 | 1.9764 | 10.3244 | 2 | 10.4 | 42.2703 | 0 | 0.075631 | 130.7713 | -0.0007372 | 0.22689 | 6.5386 | -0.0022116 | 6.7632 |  | 10.7632 | 4 | 10.7632 | 42.2703 | 21.1351 | 20 | 20 | 1.1351 | -114.8227
882 | 14.7 | 1.9766 | 10.3251 | 2 | 10.4 | 42.2798 | 0 | 0.074891 | 130.8462 | -0.00074038 | 0.22467 | 6.5423 | -0.0022211 | 6.7648 |  | 10.7648 | 4 | 10.7648 | 42.2798 | 21.1399 | 20 | 20 | 1.1399 | -113.6828
883 | 14.7167 | 1.9768 | 10.3259 | 2 | 10.4 | 42.2889 | 0 | 0.074147 | 130.9204 | -0.00074346 | 0.22244 | 6.546 | -0.0022304 | 6.7662 |  | 10.7662 | 4 | 10.7662 | 42.2889 | 21.1445 | 20 | 20 | 1.1445 | -112.5383
884 | 14.7333 | 1.9771 | 10.3266 | 2 | 10.4 | 42.2978 | 0 | 0.073401 | 130.9938 | -0.00074645 | 0.2202 | 6.5497 | -0.0022394 | 6.7677 |  | 10.7677 | 4 | 10.7677 | 42.2978 | 21.1489 | 20 | 20 | 1.1489 | -111.3894
885 | 14.75 | 1.9773 | 10.3273 | 2 | 10.4 | 42.3064 | 0 | 0.072651 | 131.0664 | -0.00074935 | 0.21795 | 6.5533 | -0.0022481 | 6.769 |  | 10.769 | 4 | 10.769 | 42.3064 | 21.1532 | 20 | 20 | 1.1532 | -110.2362
886 | 14.7667 | 1.9775 | 10.3281 | 2 | 10.4 | 42.3147 | 0 | 0.071899 | 131.1383 | -0.00075216 | 0.2157 | 6.5569 | -0.0022565 | 6.7704 |  | 10.7704 | 4 | 10.7704 | 42.3147 | 21.1574 | 20 | 20 | 1.1574 | -109.0789
887 | 14.7833 | 1.9778 | 10.3289 | 2 | 10.4 | 42.3228 | 0 | 0.071144 | 131.2095 | -0.00075487 | 0.21343 | 6.5605 | -0.0022646 | 6.7716 |  | 10.7716 | 4 | 10.7716 | 42.3228 | 21.1614 | 20 | 20 | 1.1614 | -107.9175
888 | 14.8 | 1.978 | 10.3296 | 2 | 10.4 | 42.3305 | 0 | 0.070387 | 131.2798 | -0.00075749 | 0.21116 | 6.564 | -0.0022725 | 6.7729 |  | 10.7729 | 4 | 10.7729 | 42.3305 | 21.1653 | 20 | 20 | 1.1653 | -106.7522
889 | 14.8167 | 1.9782 | 10.3304 | 2 | 10.4 | 42.338 | 0 | 0.069627 | 131.3495 | -0.00076001 | 0.20888 | 6.5675 | -0.00228 | 6.7741 |  | 10.7741 | 4 | 10.7741 | 42.338 | 21.169 | 20 | 20 | 1.169 | -105.5832
890 | 14.8333 | 1.9785 | 10.3311 | 2 | 10.4 | 42.3451 | 0 | 0.068864 | 131.4183 | -0.00076244 | 0.20659 | 6.5709 | -0.0022873 | 6.7752 |  | 10.7752 | 4 | 10.7752 | 42.3451 | 21.1726 | 20 | 20 | 1.1726 | -104.4107
891 | 14.85 | 1.9787 | 10.3319 | 2 | 10.4 | 42.352 | 0 | 0.0681 | 131.4864 | -0.00076478 | 0.2043 | 6.5743 | -0.0022944 | 6.7763 |  | 10.7763 | 4 | 10.7763 | 42.352 | 21.176 | 20 | 20 | 1.176 | -103.2347
892 | 14.8667 | 1.979 | 10.3327 | 2 | 10.4 | 42.3587 | 0 | 0.067333 | 131.5538 | -0.00076703 | 0.202 | 6.5777 | -0.0023011 | 6.7774 |  | 10.7774 | 4 | 10.7774 | 42.3587 | 21.1793 | 20 | 20 | 1.1793 | -102.0553
893 | 14.8833 | 1.9792 | 10.3334 | 2 | 10.4 | 42.365 | 0 | 0.066563 | 131.6203 | -0.00076919 | 0.19969 | 6.581 | -0.0023076 | 6.7784 |  | 10.7784 | 4 | 10.7784 | 42.365 | 21.1825 | 20 | 20 | 1.1825 | -100.8728
894 | 14.9 | 1.9794 | 10.3342 | 2 | 10.4 | 42.3711 | 0 | 0.065792 | 131.6861 | -0.00077126 | 0.19738 | 6.5843 | -0.0023138 | 6.7794 |  | 10.7794 | 4 | 10.7794 | 42.3711 | 21.1855 | 20 | 20 | 1.1855 | -99.6873
895 | 14.9167 | 1.9797 | 10.335 | 2 | 10.4 | 42.3768 | 0 | 0.065019 | 131.7511 | -0.00077324 | 0.19506 | 6.5876 | -0.0023197 | 6.7803 |  | 10.7803 | 4 | 10.7803 | 42.3768 | 21.1884 | 20 | 20 | 1.1884 | -98.4989
896 | 14.9333 | 1.9799 | 10.3358 | 2 | 10.4 | 42.3823 | 0 | 0.064244 | 131.8154 | -0.00077512 | 0.19273 | 6.5908 | -0.0023254 | 6.7812 |  | 10.7812 | 4 | 10.7812 | 42.3823 | 21.1912 | 20 | 20 | 1.1912 | -97.3077
897 | 14.95 | 1.9802 | 10.3365 | 2 | 10.4 | 42.3876 | 0 | 0.063467 | 131.8788 | -0.00077692 | 0.1904 | 6.5939 | -0.0023308 | 6.782 |  | 10.782 | 4 | 10.782 | 42.3876 | 21.1938 | 20 | 20 | 1.1938 | -96.1139
898 | 14.9667 | 1.9804 | 10.3373 | 2 | 10.4 | 42.3925 | 0 | 0.062688 | 131.9415 | -0.00077862 | 0.18806 | 6.5971 | -0.0023359 | 6.7828 |  | 10.7828 | 4 | 10.7828 | 42.3925 | 21.1963 | 20 | 20 | 1.1963 | -94.9177
899 | 14.9833 | 1.9807 | 10.3381 | 2 | 10.4 | 42.3972 | 0 | 0.061908 | 132.0034 | -0.00078024 | 0.18572 | 6.6002 | -0.0023407 | 6.7836 |  | 10.7836 | 4 | 10.7836 | 42.3972 | 21.1986 | 20 | 20 | 1.1986 | -93.719
900 | 15 | 1.9809 | 10.3389 | 2 | 10.4 | 42.4016 | 0 | 0.061126 | 132.0646 | -0.00078177 | 0.18338 | 6.6032 | -0.0023453 | 6.7843 |  | 10.7843 | 4 | 10.7843 | 42.4016 | 21.2008 | 20 | 20 | 1.2008 | -92.5182
901 | 15.0167 | 1.9811 | 10.3397 | 2 | 10.4 | 42.4058 | 0 | 0.060343 | 132.1249 | -0.00078321 | 0.18103 | 6.6062 | -0.0023496 | 6.7849 |  | 10.7849 | 4 | 10.7849 | 42.4058 | 21.2029 | 20 | 20 | 1.2029 | -91.3153
902 | 15.0333 | 1.9814 | 10.3404 | 2 | 10.4 | 42.4097 | 0 | 0.059559 | 132.1845 | -0.00078456 | 0.17868 | 6.6092 | -0.0023537 | 6.7855 |  | 10.7855 | 4 | 10.7855 | 42.4097 | 21.2048 | 20 | 20 | 1.2048 | -90.1105
903 | 15.05 | 1.9816 | 10.3412 | 2 | 10.4 | 42.4133 | 0 | 0.058773 | 132.2432 | -0.00078583 | 0.17632 | 6.6122 | -0.0023575 | 6.7861 |  | 10.7861 | 4 | 10.7861 | 42.4133 | 21.2066 | 20 | 20 | 1.2066 | -88.9039
904 | 15.0667 | 1.9819 | 10.342 | 2 | 10.4 | 42.4166 | 0 | 0.057986 | 132.3012 | -0.000787 | 0.17396 | 6.6151 | -0.002361 | 6.7867 |  | 10.7867 | 4 | 10.7867 | 42.4166 | 21.2083 | 20 | 20 | 1.2083 | -87.6956
905 | 15.0833 | 1.9821 | 10.3428 | 2 | 10.4 | 42.4197 | 0 | 0.057198 | 132.3584 | -0.00078809 | 0.17159 | 6.6179 | -0.0023643 | 6.7871 |  | 10.7871 | 4 | 10.7871 | 42.4197 | 21.2098 | 20 | 20 | 1.2098 | -86.4857
906 | 15.1 | 1.9824 | 10.3436 | 2 | 10.4 | 42.4225 | 0 | 0.056409 | 132.4148 | -0.0007891 | 0.16923 | 6.6207 | -0.0023673 | 6.7876 |  | 10.7876 | 4 | 10.7876 | 42.4225 | 21.2113 | 20 | 20 | 1.2113 | -85.2745
907 | 15.1167 | 1.9826 | 10.3444 | 2 | 10.4 | 42.4251 | 0 | 0.055619 | 132.4705 | -0.00079001 | 0.16686 | 6.6235 | -0.00237 | 6.788 |  | 10.788 | 4 | 10.788 | 42.4251 | 21.2125 | 20 | 20 | 1.2125 | -84.0619
908 | 15.1333 | 1.9829 | 10.3452 | 2 | 10.4 | 42.4273 | 0 | 0.054828 | 132.5253 | -0.00079084 | 0.16448 | 6.6263 | -0.0023725 | 6.7884 |  | 10.7884 | 4 | 10.7884 | 42.4273 | 21.2137 | 20 | 20 | 1.2137 | -82.8483
909 | 15.15 | 1.9831 | 10.346 | 2 | 10.4 | 42.4294 | 0 | 0.054036 | 132.5793 | -0.00079159 | 0.16211 | 6.629 | -0.0023748 | 6.7887 |  | 10.7887 | 4 | 10.7887 | 42.4294 | 21.2147 | 20 | 20 | 1.2147 | -81.6336
910 | 15.1667 | 1.9834 | 10.3468 | 2 | 10.4 | 42.4311 | 0 | 0.053244 | 132.6326 | -0.00079225 | 0.15973 | 6.6316 | -0.0023768 | 6.789 |  | 10.789 | 4 | 10.789 | 42.4311 | 21.2156 | 20 | 20 | 1.2156 | -80.418
911 | 15.1833 | 1.9836 | 10.3475 | 2 | 10.4 | 42.4327 | 0 | 0.052451 | 132.685 | -0.00079283 | 0.15735 | 6.6343 | -0.0023785 | 6.7892 |  | 10.7892 | 4 | 10.7892 | 42.4327 | 21.2163 | 20 | 20 | 1.2163 | -79.2017
912 | 15.2 | 1.9839 | 10.3483 | 2 | 10.4 | 42.4339 | 0 | 0.051658 | 132.7367 | -0.00079333 | 0.15497 | 6.6368 | -0.00238 | 6.7894 |  | 10.7894 | 4 | 10.7894 | 42.4339 | 21.217 | 20 | 20 | 1.217 | -77.9847
913 | 15.2167 | 1.9841 | 10.3491 | 2 | 10.4 | 42.4349 | 0 | 0.050864 | 132.7875 | -0.00079374 | 0.15259 | 6.6394 | -0.0023812 | 6.7896 |  | 10.7896 | 4 | 10.7896 | 42.4349 | 21.2175 | 20 | 20 | 1.2175 | -76.7673
914 | 15.2333 | 1.9844 | 10.3499 | 2 | 10.4 | 42.4357 | 0 | 0.05007 | 132.8376 | -0.00079406 | 0.15021 | 6.6419 | -0.0023822 | 6.7897 |  | 10.7897 | 4 | 10.7897 | 42.4357 | 21.2178 | 20 | 20 | 1.2178 | -75.5494
915 | 15.25 | 1.9846 | 10.3507 | 2 | 10.4 | 42.4362 | 0 | 0.049276 | 132.8869 | -0.00079431 | 0.14783 | 6.6443 | -0.0023829 | 6.7898 |  | 10.7898 | 4 | 10.7898 | 42.4362 | 21.2181 | 20 | 20 | 1.2181 | -74.3313
916 | 15.2667 | 1.9848 | 10.3515 | 2 | 10.4 | 42.4364 | 0 | 0.048481 | 132.9354 | -0.00079447 | 0.14544 | 6.6468 | -0.0023834 | 6.7898 |  | 10.7898 | 4 | 10.7898 | 42.4364 | 21.2182 | 20 | 20 | 1.2182 | -73.1131
917 | 15.2833 | 1.9851 | 10.3523 | 2 | 10.4 | 42.4364 | 0 | 0.047687 | 132.983 | -0.00079455 | 0.14306 | 6.6492 | -0.0023837 | 6.7898 |  | 10.7898 | 4 | 10.7898 | 42.4364 | 21.2182 | 20 | 20 | 1.2182 | -71.8949
918 | 15.3 | 1.9853 | 10.3531 | 2 | 10.4 | 42.4362 | 0 | 0.046892 | 133.0299 | -0.00079455 | 0.14068 | 6.6515 | -0.0023837 | 6.7898 |  | 10.7898 | 4 | 10.7898 | 42.4362 | 21.2181 | 20 | 20 | 1.2181 | -70.6768
919 | 15.3167 | 1.9856 | 10.3539 | 2 | 10.4 | 42.4357 | 0 | 0.046097 | 133.076 | -0.00079447 | 0.13829 | 6.6538 | -0.0023834 | 6.7897 |  | 10.7897 | 4 | 10.7897 | 42.4357 | 21.2178 | 20 | 20 | 1.2178 | -69.459
920 | 15.3333 | 1.9858 | 10.3547 | 2 | 10.4 | 42.435 | 0 | 0.045303 | 133.1213 | -0.00079432 | 0.13591 | 6.6561 | -0.0023829 | 6.7896 |  | 10.7896 | 4 | 10.7896 | 42.435 | 21.2175 | 20 | 20 | 1.2175 | -68.2415
921 | 15.35 | 1.9861 | 10.3555 | 2 | 10.4 | 42.434 | 0 | 0.044509 | 133.1658 | -0.00079408 | 0.13353 | 6.6583 | -0.0023822 | 6.7894 |  | 10.7894 | 4 | 10.7894 | 42.434 | 21.217 | 20 | 20 | 1.217 | -67.0245
922 | 15.3667 | 1.9863 | 10.3563 | 2 | 10.4 | 42.4328 | 0 | 0.043715 | 133.2096 | -0.00079376 | 0.13115 | 6.6605 | -0.0023813 | 6.7892 |  | 10.7892 | 4 | 10.7892 | 42.4328 | 21.2164 | 20 | 20 | 1.2164 | -65.8081
923 | 15.3833 | 1.9866 | 10.3571 | 2 | 10.4 | 42.4313 | 0 | 0.042922 | 133.2525 | -0.00079336 | 0.12877 | 6.6626 | -0.0023801 | 6.789 |  | 10.789 | 4 | 10.789 | 42.4313 | 21.2157 | 20 | 20 | 1.2157 | -64.5925
924 | 15.4 | 1.9868 | 10.3579 | 2 | 10.4 | 42.4296 | 0 | 0.042129 | 133.2946 | -0.00079289 | 0.12639 | 6.6647 | -0.0023787 | 6.7887 |  | 10.7887 | 4 | 10.7887 | 42.4296 | 21.2148 | 20 | 20 | 1.2148 | -63.3777
925 | 15.4167 | 1.9871 | 10.3587 | 2 | 10.4 | 42.4277 | 0 | 0.041337 | 133.336 | -0.00079234 | 0.12401 | 6.6668 | -0.002377 | 6.7884 |  | 10.7884 | 4 | 10.7884 | 42.4277 | 21.2138 | 20 | 20 | 1.2138 | -62.1638
926 | 15.4333 | 1.9873 | 10.3595 | 2 | 10.4 | 42.4255 | 0 | 0.040545 | 133.3765 | -0.00079171 | 0.12164 | 6.6688 | -0.0023751 | 6.7881 |  | 10.7881 | 4 | 10.7881 | 42.4255 | 21.2128 | 20 | 20 | 1.2128 | -60.951
927 | 15.45 | 1.9876 | 10.3602 | 2 | 10.4 | 42.4231 | 0 | 0.039754 | 133.4163 | -0.000791 | 0.11926 | 6.6708 | -0.002373 | 6.7877 |  | 10.7877 | 4 | 10.7877 | 42.4231 | 21.2116 | 20 | 20 | 1.2116 | -59.7395
928 | 15.4667 | 1.9878 | 10.361 | 2 | 10.4 | 42.4205 | 0 | 0.038964 | 133.4552 | -0.00079022 | 0.11689 | 6.6728 | -0.0023707 | 6.7873 |  | 10.7873 | 4 | 10.7873 | 42.4205 | 21.2103 | 20 | 20 | 1.2103 | -58.5292
929 | 15.4833 | 1.9881 | 10.3618 | 2 | 10.4 | 42.4177 | 0 | 0.038174 | 133.4934 | -0.00078936 | 0.11452 | 6.6747 | -0.0023681 | 6.7868 |  | 10.7868 | 4 | 10.7868 | 42.4177 | 21.2088 | 20 | 20 | 1.2088 | -57.3204
930 | 15.5 | 1.9883 | 10.3626 | 2 | 10.4 | 42.4146 | 0 | 0.037386 | 133.5308 | -0.00078843 | 0.11216 | 6.6765 | -0.0023653 | 6.7863 |  | 10.7863 | 4 | 10.7863 | 42.4146 | 21.2073 | 20 | 20 | 1.2073 | -56.1131
931 | 15.5167 | 1.9886 | 10.3634 | 2 | 10.4 | 42.4113 | 0 | 0.036599 | 133.5674 | -0.00078743 | 0.1098 | 6.6784 | -0.0023623 | 6.7858 |  | 10.7858 | 4 | 10.7858 | 42.4113 | 21.2056 | 20 | 20 | 1.2056 | -54.9075
932 | 15.5333 | 1.9888 | 10.3642 | 2 | 10.4 | 42.4077 | 0 | 0.035812 | 133.6032 | -0.00078635 | 0.10744 | 6.6802 | -0.002359 | 6.7852 |  | 10.7852 | 4 | 10.7852 | 42.4077 | 21.2039 | 20 | 20 | 1.2039 | -53.7036
933 | 15.55 | 1.9891 | 10.365 | 2 | 10.4 | 42.404 | 0 | 0.035027 | 133.6382 | -0.0007852 | 0.10508 | 6.6819 | -0.0023556 | 6.7846 |  | 10.7846 | 4 | 10.7846 | 42.404 | 21.202 | 20 | 20 | 1.202 | -52.5016
934 | 15.5667 | 1.9893 | 10.3658 | 2 | 10.4 | 42.4 | 0 | 0.034243 | 133.6725 | -0.00078397 | 0.10273 | 6.6836 | -0.0023519 | 6.784 |  | 10.784 | 4 | 10.784 | 42.4 | 21.2 | 20 | 20 | 1.2 | -51.3016
935 | 15.5833 | 1.9895 | 10.3665 | 2 | 10.4 | 42.3958 | 0 | 0.03346 | 133.7059 | -0.00078268 | 0.10038 | 6.6853 | -0.002348 | 6.7833 |  | 10.7833 | 4 | 10.7833 | 42.3958 | 21.1979 | 20 | 20 | 1.1979 | -50.1037
936 | 15.6 | 1.9898 | 10.3673 | 2 | 10.4 | 42.3914 | 0 | 0.032679 | 133.7386 | -0.00078131 | 0.098037 | 6.6869 | -0.0023439 | 6.7826 |  | 10.7826 | 4 | 10.7826 | 42.3914 | 21.1957 | 20 | 20 | 1.1957 | -48.908
937 | 15.6167 | 1.99 | 10.3681 | 2 | 10.4 | 42.3868 | 0 | 0.031899 | 133.7705 | -0.00077987 | 0.095698 | 6.6885 | -0.0023396 | 6.7819 |  | 10.7819 | 4 | 10.7819 | 42.3868 | 21.1934 | 20 | 20 | 1.1934 | -47.7146
938 | 15.6333 | 1.9903 | 10.3689 | 2 | 10.4 | 42.3819 | 0 | 0.031121 | 133.8016 | -0.00077836 | 0.093363 | 6.6901 | -0.0023351 | 6.7811 |  | 10.7811 | 4 | 10.7811 | 42.3819 | 21.191 | 20 | 20 | 1.191 | -46.5237
939 | 15.65 | 1.9905 | 10.3697 | 2 | 10.4 | 42.3769 | 0 | 0.030344 | 133.832 | -0.00077678 | 0.091032 | 6.6916 | -0.0023303 | 6.7803 |  | 10.7803 | 4 | 10.7803 | 42.3769 | 21.1884 | 20 | 20 | 1.1884 | -45.3352
940 | 15.6667 | 1.9908 | 10.3704 | 2 | 10.4 | 42.3716 | 0 | 0.029569 | 133.8615 | -0.00077513 | 0.088707 | 6.6931 | -0.0023254 | 6.7795 |  | 10.7795 | 4 | 10.7795 | 42.3716 | 21.1858 | 20 | 20 | 1.1858 | -44.1494
941 | 15.6833 | 1.991 | 10.3712 | 2 | 10.4 | 42.3661 | 0 | 0.028796 | 133.8903 | -0.00077342 | 0.086387 | 6.6945 | -0.0023203 | 6.7786 |  | 10.7786 | 4 | 10.7786 | 42.3661 | 21.1831 | 20 | 20 | 1.1831 | -42.9664
942 | 15.7 | 1.9912 | 10.372 | 2 | 10.4 | 42.3605 | 0 | 0.028024 | 133.9183 | -0.00077163 | 0.084072 | 6.6959 | -0.0023149 | 6.7777 |  | 10.7777 | 4 | 10.7777 | 42.3605 | 21.1802 | 20 | 20 | 1.1802 | -41.7861
943 | 15.7167 | 1.9915 | 10.3727 | 2 | 10.4 | 42.3546 | 0 | 0.027254 | 133.9456 | -0.00076978 | 0.081762 | 6.6973 | -0.0023093 | 6.7767 |  | 10.7767 | 4 | 10.7767 | 42.3546 | 21.1773 | 20 | 20 | 1.1773 | -40.6088
944 | 15.7333 | 1.9917 | 10.3735 | 2 | 10.4 | 42.3485 | 0 | 0.026486 | 133.9721 | -0.00076786 | 0.079459 | 6.6986 | -0.0023036 | 6.7758 |  | 10.7758 | 4 | 10.7758 | 42.3485 | 21.1742 | 20 | 20 | 1.1742 | -39.4346
945 | 15.75 | 1.992 | 10.3743 | 2 | 10.4 | 42.3422 | 0 | 0.02572 | 133.9978 | -0.00076588 | 0.077161 | 6.6999 | -0.0022976 | 6.7748 |  | 10.7748 | 4 | 10.7748 | 42.3422 | 21.1711 | 20 | 20 | 1.1711 | -38.2635
946 | 15.7667 | 1.9922 | 10.375 | 2 | 10.4 | 42.3357 | 0 | 0.024957 | 134.0228 | -0.00076383 | 0.07487 | 6.7011 | -0.0022915 | 6.7737 |  | 10.7737 | 4 | 10.7737 | 42.3357 | 21.1679 | 20 | 20 | 1.1679 | -37.0956
947 | 15.7833 | 1.9924 | 10.3758 | 2 | 10.4 | 42.329 | 0 | 0.024195 | 134.047 | -0.00076172 | 0.072585 | 6.7023 | -0.0022851 | 6.7726 |  | 10.7726 | 4 | 10.7726 | 42.329 | 21.1645 | 20 | 20 | 1.1645 | -35.9311
948 | 15.8 | 1.9927 | 10.3766 | 2 | 10.4 | 42.3222 | 0 | 0.023435 | 134.0704 | -0.00075954 | 0.070306 | 6.7035 | -0.0022786 | 6.7715 |  | 10.7715 | 4 | 10.7715 | 42.3222 | 21.1611 | 20 | 20 | 1.1611 | -34.77
949 | 15.8167 | 1.9929 | 10.3773 | 2 | 10.4 | 42.3151 | 0 | 0.022678 | 134.0931 | -0.00075729 | 0.068034 | 6.7047 | -0.0022719 | 6.7704 |  | 10.7704 | 4 | 10.7704 | 42.3151 | 21.1575 | 20 | 20 | 1.1575 | -33.6125
950 | 15.8333 | 1.9931 | 10.3781 | 2 | 10.4 | 42.3078 | 0 | 0.021923 | 134.115 | -0.00075499 | 0.065769 | 6.7057 | -0.002265 | 6.7693 |  | 10.7693 | 4 | 10.7693 | 42.3078 | 21.1539 | 20 | 20 | 1.1539 | -32.4585
951 | 15.85 | 1.9934 | 10.3788 | 2 | 10.4 | 42.3004 | 0 | 0.02117 | 134.1362 | -0.00075262 | 0.063511 | 6.7068 | -0.0022579 | 6.7681 |  | 10.7681 | 4 | 10.7681 | 42.3004 | 21.1502 | 20 | 20 | 1.1502 | -31.3083
952 | 15.8667 | 1.9936 | 10.3796 | 2 | 10.4 | 42.2927 | 0 | 0.02042 | 134.1566 | -0.00075019 | 0.061261 | 6.7078 | -0.0022506 | 6.7668 |  | 10.7668 | 4 | 10.7668 | 42.2927 | 21.1464 | 20 | 20 | 1.1464 | -30.162
953 | 15.8833 | 1.9939 | 10.3803 | 2 | 10.4 | 42.2849 | 0 | 0.019673 | 134.1763 | -0.0007477 | 0.059018 | 6.7088 | -0.0022431 | 6.7656 |  | 10.7656 | 4 | 10.7656 | 42.2849 | 21.1425 | 20 | 20 | 1.1425 | -29.0195
954 | 15.9 | 1.9941 | 10.3811 | 2 | 10.4 | 42.2769 | 0 | 0.018927 | 134.1952 | -0.00074515 | 0.056782 | 6.7098 | -0.0022354 | 6.7643 |  | 10.7643 | 4 | 10.7643 | 42.2769 | 21.1385 | 20 | 20 | 1.1385 | -27.8811
955 | 15.9167 | 1.9943 | 10.3818 | 2 | 10.4 | 42.2687 | 0 | 0.018185 | 134.2134 | -0.00074253 | 0.054555 | 6.7107 | -0.0022276 | 6.763 |  | 10.763 | 4 | 10.763 | 42.2687 | 21.1344 | 20 | 20 | 1.1344 | -26.7467
956 | 15.9333 | 1.9945 | 10.3826 | 2 | 10.4 | 42.2604 | 0 | 0.017445 | 134.2308 | -0.00073986 | 0.052335 | 6.7115 | -0.0022196 | 6.7617 |  | 10.7617 | 4 | 10.7617 | 42.2604 | 21.1302 | 20 | 20 | 1.1302 | -25.6165
957 | 15.95 | 1.9948 | 10.3833 | 2 | 10.4 | 42.2518 | 0 | 0.016708 | 134.2475 | -0.00073713 | 0.050124 | 6.7124 | -0.0022114 | 6.7603 |  | 10.7603 | 4 | 10.7603 | 42.2518 | 21.1259 | 20 | 20 | 1.1259 | -24.4906
958 | 15.9667 | 1.995 | 10.384 | 2 | 10.4 | 42.2431 | 0 | 0.015973 | 134.2635 | -0.00073435 | 0.04792 | 6.7132 | -0.002203 | 6.7589 |  | 10.7589 | 4 | 10.7589 | 42.2431 | 21.1215 | 20 | 20 | 1.1215 | -23.3691
959 | 15.9833 | 1.9952 | 10.3848 | 2 | 10.4 | 42.2342 | 0 | 0.015242 | 134.2787 | -0.0007315 | 0.045726 | 6.7139 | -0.0021945 | 6.7575 |  | 10.7575 | 4 | 10.7575 | 42.2342 | 21.1171 | 20 | 20 | 1.1171 | -22.252
960 | 16 | 1.9955 | 10.3855 | 2 | 10.4 | 42.2251 | 0 | 0.014513 | 134.2933 | -0.0007286 | 0.04354 | 6.7147 | -0.0021858 | 6.756 |  | 10.756 | 4 | 10.756 | 42.2251 | 21.1126 | 20 | 20 | 1.1126 | -21.1394
961 | 16.0167 | 1.9957 | 10.3862 | 2 | 10.4 | 42.2159 | 0 | 0.013788 | 134.307 | -0.00072564 | 0.041363 | 6.7154 | -0.0021769 | 6.7545 |  | 10.7545 | 4 | 10.7545 | 42.2159 | 21.1079 | 20 | 20 | 1.1079 | -20.0315
962 | 16.0333 | 1.9959 | 10.3869 | 2 | 10.4 | 42.2065 | 0 | 0.013065 | 134.3201 | -0.00072263 | 0.039195 | 6.716 | -0.0021679 | 6.753 |  | 10.753 | 4 | 10.753 | 42.2065 | 21.1032 | 20 | 20 | 1.1032 | -18.9283
963 | 16.05 | 1.9961 | 10.3877 | 2 | 10.4 | 42.1969 | 0 | 0.012346 | 134.3325 | -0.00071956 | 0.037037 | 6.7166 | -0.0021587 | 6.7515 |  | 10.7515 | 4 | 10.7515 | 42.1969 | 21.0984 | 20 | 20 | 1.0984 | -17.8298
964 | 16.0667 | 1.9964 | 10.3884 | 2 | 10.4 | 42.1871 | 0 | 0.011629 | 134.3441 | -0.00071643 | 0.034887 | 6.7172 | -0.0021493 | 6.7499 |  | 10.7499 | 4 | 10.7499 | 42.1871 | 21.0936 | 20 | 20 | 1.0936 | -16.7363
965 | 16.0833 | 1.9966 | 10.3891 | 2 | 10.4 | 42.1772 | 0 | 0.010916 | 134.355 | -0.00071326 | 0.032748 | 6.7177 | -0.0021398 | 6.7484 |  | 10.7484 | 4 | 10.7484 | 42.1772 | 21.0886 | 20 | 20 | 1.0886 | -15.6476
966 | 16.1 | 1.9968 | 10.3898 | 2 | 10.4 | 42.1672 | 0 | 0.010206 | 134.3652 | -0.00071003 | 0.030618 | 6.7183 | -0.0021301 | 6.7467 |  | 10.7467 | 4 | 10.7467 | 42.1672 | 21.0836 | 20 | 20 | 1.0836 | -14.5641
967 | 16.1167 | 1.997 | 10.3905 | 2 | 10.4 | 42.157 | 0 | 0.0094991 | 134.3747 | -0.00070675 | 0.028497 | 6.7187 | -0.0021202 | 6.7451 |  | 10.7451 | 4 | 10.7451 | 42.157 | 21.0785 | 20 | 20 | 1.0785 | -13.4856
968 | 16.1333 | 1.9973 | 10.3912 | 2 | 10.4 | 42.1466 | 0 | 0.0087957 | 134.3835 | -0.00070341 | 0.026387 | 6.7192 | -0.0021102 | 6.7435 |  | 10.7435 | 4 | 10.7435 | 42.1466 | 21.0733 | 20 | 20 | 1.0733 | -12.4123
969 | 16.15 | 1.9975 | 10.3919 | 2 | 10.4 | 42.136 | 0 | 0.0080957 | 134.3916 | -0.00070003 | 0.024287 | 6.7196 | -0.0021001 | 6.7418 |  | 10.7418 | 4 | 10.7418 | 42.136 | 21.068 | 20 | 20 | 1.068 | -11.3443
970 | 16.1667 | 1.9977 | 10.3926 | 2 | 10.4 | 42.1254 | 0 | 0.0073991 | 134.399 | -0.00069659 | 0.022197 | 6.7199 | -0.0020898 | 6.7401 |  | 10.7401 | 4 | 10.7401 | 42.1254 | 21.0627 | 20 | 20 | 1.0627 | -10.2816
971 | 16.1833 | 1.9979 | 10.3933 | 2 | 10.4 | 42.1145 | 0 | 0.006706 | 134.4057 | -0.00069311 | 0.020118 | 6.7203 | -0.0020793 | 6.7383 |  | 10.7383 | 4 | 10.7383 | 42.1145 | 21.0573 | 20 | 20 | 1.0573 | -9.2243
972 | 16.2 | 1.9981 | 10.394 | 2 | 10.4 | 42.1035 | 0 | 0.0060164 | 134.4117 | -0.00068958 | 0.018049 | 6.7206 | -0.0020687 | 6.7366 |  | 10.7366 | 4 | 10.7366 | 42.1035 | 21.0518 | 20 | 20 | 1.0518 | -8.1726
973 | 16.2167 | 1.9983 | 10.3947 | 2 | 10.4 | 42.0924 | 0 | 0.0053304 | 134.417 | -0.00068599 | 0.015991 | 6.7209 | -0.002058 | 6.7348 |  | 10.7348 | 4 | 10.7348 | 42.0924 | 21.0462 | 20 | 20 | 1.0462 | -7.1264
974 | 16.2333 | 1.9985 | 10.3954 | 2 | 10.4 | 42.0811 | 0 | 0.004648 | 134.4217 | -0.00068237 | 0.013944 | 6.7211 | -0.0020471 | 6.733 |  | 10.733 | 4 | 10.733 | 42.0811 | 21.0406 | 20 | 20 | 1.0406 | -6.0858
975 | 16.25 | 1.9988 | 10.396 | 2 | 10.4 | 42.0697 | 0 | 0.0039693 | 134.4257 | -0.00067869 | 0.011908 | 6.7213 | -0.0020361 | 6.7312 |  | 10.7312 | 4 | 10.7312 | 42.0697 | 21.0349 | 20 | 20 | 1.0349 | -5.0509
976 | 16.2667 | 1.999 | 10.3967 | 2 | 10.4 | 42.0582 | 0 | 0.0032944 | 134.429 | -0.00067497 | 0.0098831 | 6.7214 | -0.0020249 | 6.7293 |  | 10.7293 | 4 | 10.7293 | 42.0582 | 21.0291 | 20 | 20 | 1.0291 | -4.0219
977 | 16.2833 | 1.9992 | 10.3974 | 2 | 10.4 | 42.0465 | 0 | 0.0026232 | 134.4316 | -0.0006712 | 0.0078695 | 6.7216 | -0.0020136 | 6.7274 |  | 10.7274 | 4 | 10.7274 | 42.0465 | 21.0232 | 20 | 20 | 1.0232 | -2.9986
978 | 16.3 | 1.9994 | 10.398 | 2 | 10.4 | 42.0346 | 0 | 0.0019558 | 134.4335 | -0.00066738 | 0.0058674 | 6.7217 | -0.0020022 | 6.7255 |  | 10.7255 | 4 | 10.7255 | 42.0346 | 21.0173 | 20 | 20 | 1.0173 | -1.9813
979 | 16.3167 | 1.9996 | 10.3987 | 2 | 10.4 | 42.0227 | 0 | 0.0012923 | 134.4348 | -0.00066353 | 0.0038768 | 6.7217 | -0.0019906 | 6.7236 |  | 10.7236 | 4 | 10.7236 | 42.0227 | 21.0113 | 20 | 20 | 1.0113 | -0.96997
980 | 16.3333 | 1.9998 | 10.3994 | 2 | 10.4 | 42.0106 | 0 | 0.00063264 | 134.4355 | -0.00065962 | 0.0018979 | 6.7218 | -0.0019789 | 6.7217 |  | 10.7217 | 4 | 10.7217 | 42.0106 | 21.0053 | 20 | 20 | 1.0053 | 0.035322
981 | 16.35 | 2 | 10.4 | 2 | 10.4 | 41.9983 | 0 | -2.3038e-05 | 134.4354 | -0.00065568 | -6.9114e-05 | 6.7218 | -0.001967 | 6.7197 |  | 10.7197 | 4 | 10.7197 | 41.9983 | 20.9992 | 20 | 20 | 0.99917 | 1.0345
982 | 16.3667 | 2.0002 | 10.4007 | 2 | 10.4 | 41.986 | 0 | -0.00067473 | 134.4348 | -0.00065169 | -0.0020242 | 6.7217 | -0.0019551 | 6.7178 |  | 10.7178 | 4 | 10.7178 | 41.986 | 20.993 | 20 | 20 | 0.993 | 2.0275
983 | 16.3833 | 2.0004 | 10.4013 | 2 | 10.4 | 41.9735 | 0 | -0.0013224 | 134.4334 | -0.00064766 | -0.0039672 | 6.7217 | -0.001943 | 6.7158 |  | 10.7158 | 4 | 10.7158 | 41.9735 | 20.9868 | 20 | 20 | 0.98676 | 3.0142
984 | 16.4 | 2.0006 | 10.402 | 2 | 10.4 | 41.9609 | 0 | -0.001966 | 134.4315 | -0.00064359 | -0.0058979 | 6.7216 | -0.0019308 | 6.7137 |  | 10.7137 | 4 | 10.7137 | 41.9609 | 20.9805 | 20 | 20 | 0.98045 | 3.9947
985 | 16.4167 | 2.0008 | 10.4026 | 2 | 10.4 | 41.9482 | 0 | -0.0026055 | 134.4289 | -0.00063948 | -0.0078164 | 6.7214 | -0.0019184 | 6.7117 |  | 10.7117 | 4 | 10.7117 | 41.9482 | 20.9741 | 20 | 20 | 0.97409 | 4.9688
986 | 16.4333 | 2.001 | 10.4032 | 2 | 10.4 | 41.9353 | 0 | -0.0032408 | 134.4256 | -0.00063533 | -0.0097224 | 6.7213 | -0.001906 | 6.7097 |  | 10.7097 | 4 | 10.7097 | 41.9353 | 20.9677 | 20 | 20 | 0.96767 | 5.9365
987 | 16.45 | 2.0012 | 10.4039 | 2 | 10.4 | 41.9224 | 0 | -0.0038719 | 134.4218 | -0.00063114 | -0.011616 | 6.7211 | -0.0018934 | 6.7076 |  | 10.7076 | 4 | 10.7076 | 41.9224 | 20.9612 | 20 | 20 | 0.96118 | 6.8976
988 | 16.4667 | 2.0014 | 10.4045 | 2 | 10.4 | 41.9093 | 0 | -0.0044988 | 134.4173 | -0.00062691 | -0.013497 | 6.7209 | -0.0018807 | 6.7055 |  | 10.7055 | 4 | 10.7055 | 41.9093 | 20.9546 | 20 | 20 | 0.95464 | 7.8523
989 | 16.4833 | 2.0016 | 10.4051 | 2 | 10.4 | 41.8961 | 0 | -0.0051215 | 134.4121 | -0.00062265 | -0.015364 | 6.7206 | -0.0018679 | 6.7034 |  | 10.7034 | 4 | 10.7034 | 41.8961 | 20.948 | 20 | 20 | 0.94805 | 8.8003
990 | 16.5 | 2.0018 | 10.4057 | 2 | 10.4 | 41.8828 | 0 | -0.0057398 | 134.4064 | -0.00061834 | -0.017219 | 6.7203 | -0.001855 | 6.7012 |  | 10.7012 | 4 | 10.7012 | 41.8828 | 20.9414 | 20 | 20 | 0.94139 | 9.7417
991 | 16.5167 | 2.002 | 10.4064 | 2 | 10.4 | 41.8694 | 0 | -0.0063538 | 134.4 | -0.000614 | -0.019062 | 6.72 | -0.001842 | 6.6991 |  | 10.6991 | 4 | 10.6991 | 41.8694 | 20.9347 | 20 | 20 | 0.93468 | 10.6764
992 | 16.5333 | 2.0022 | 10.407 | 2 | 10.4 | 41.8558 | 0 | -0.0069635 | 134.3931 | -0.00060963 | -0.02089 | 6.7197 | -0.0018289 | 6.6969 |  | 10.6969 | 4 | 10.6969 | 41.8558 | 20.9279 | 20 | 20 | 0.92792 | 11.6043
993 | 16.55 | 2.0024 | 10.4076 | 2 | 10.4 | 41.8422 | 0 | -0.0075687 | 134.3855 | -0.00060522 | -0.022706 | 6.7193 | -0.0018157 | 6.6948 |  | 10.6948 | 4 | 10.6948 | 41.8422 | 20.9211 | 20 | 20 | 0.92111 | 12.5254
994 | 16.5667 | 2.0026 | 10.4082 | 2 | 10.4 | 41.8285 | 0 | -0.0081695 | 134.3773 | -0.00060077 | -0.024508 | 6.7189 | -0.0018023 | 6.6926 |  | 10.6926 | 4 | 10.6926 | 41.8285 | 20.9142 | 20 | 20 | 0.91424 | 13.4397
995 | 16.5833 | 2.0027 | 10.4088 | 2 | 10.4 | 41.8146 | 0 | -0.0087657 | 134.3686 | -0.00059629 | -0.026297 | 6.7184 | -0.0017889 | 6.6903 |  | 10.6903 | 4 | 10.6903 | 41.8146 | 20.9073 | 20 | 20 | 0.90732 | 14.347
996 | 16.6 | 2.0029 | 10.4094 | 2 | 10.4 | 41.8007 | 0 | -0.0093575 | 134.3592 | -0.00059178 | -0.028073 | 6.718 | -0.0017753 | 6.6881 |  | 10.6881 | 4 | 10.6881 | 41.8007 | 20.9004 | 20 | 20 | 0.90035 | 15.2473
997 | 16.6167 | 2.0031 | 10.4099 | 2 | 10.4 | 41.7867 | 0 | -0.0099448 | 134.3493 | -0.00058724 | -0.029834 | 6.7175 | -0.0017617 | 6.6859 |  | 10.6859 | 4 | 10.6859 | 41.7867 | 20.8933 | 20 | 20 | 0.89334 | 16.1407
998 | 16.6333 | 2.0033 | 10.4105 | 2 | 10.4 | 41.7725 | 0 | -0.010527 | 134.3387 | -0.00058266 | -0.031582 | 6.7169 | -0.001748 | 6.6836 |  | 10.6836 | 4 | 10.6836 | 41.7725 | 20.8863 | 20 | 20 | 0.88627 | 17.027
999 | 16.65 | 2.0035 | 10.4111 | 2 | 10.4 | 41.7583 | 0 | -0.011105 | 134.3276 | -0.00057805 | -0.033316 | 6.7164 | -0.0017342 | 6.6813 |  | 10.6813 | 4 | 10.6813 | 41.7583 | 20.8792 | 20 | 20 | 0.87916 | 17.9061
1000 | 16.6667 | 2.0036 | 10.4117 | 2 | 10.4 | 41.744 | 0 | -0.011679 | 134.316 | -0.00057341 | -0.035037 | 6.7158 | -0.0017202 | 6.679 |  | 10.679 | 4 | 10.679 | 41.744 | 20.872 | 20 | 20 | 0.872 | 18.7781
1001 | 16.6833 | 2.0038 | 10.4122 | 2 | 10.4 | 41.7296 | 0 | -0.012248 | 134.3037 | -0.00056875 | -0.036743 | 6.7152 | -0.0017062 | 6.6767 |  | 10.6767 | 4 | 10.6767 | 41.7296 | 20.8648 | 20 | 20 | 0.8648 | 19.6429
1002 | 16.7 | 2.004 | 10.4128 | 2 | 10.4 | 41.7151 | 0 | -0.012812 | 134.2909 | -0.00056405 | -0.038435 | 6.7145 | -0.0016921 | 6.6744 |  | 10.6744 | 4 | 10.6744 | 41.7151 | 20.8576 | 20 | 20 | 0.85756 | 20.5005
1003 | 16.7167 | 2.0042 | 10.4134 | 2 | 10.4 | 41.7005 | 0 | -0.013371 | 134.2775 | -0.00055932 | -0.040113 | 6.7139 | -0.001678 | 6.6721 |  | 10.6721 | 4 | 10.6721 | 41.7005 | 20.8503 | 20 | 20 | 0.85027 | 21.3507
1004 | 16.7333 | 2.0044 | 10.4139 | 2 | 10.4 | 41.6859 | 0 | -0.013926 | 134.2636 | -0.00055457 | -0.041777 | 6.7132 | -0.0016637 | 6.6697 |  | 10.6697 | 4 | 10.6697 | 41.6859 | 20.8429 | 20 | 20 | 0.84294 | 22.1937
1005 | 16.75 | 2.0045 | 10.4145 | 2 | 10.4 | 41.6711 | 0 | -0.014475 | 134.2491 | -0.00054979 | -0.043426 | 6.7125 | -0.0016494 | 6.6674 |  | 10.6674 | 4 | 10.6674 | 41.6711 | 20.8356 | 20 | 20 | 0.83557 | 23.0292
1006 | 16.7667 | 2.0047 | 10.415 | 2 | 10.4 | 41.6563 | 0 | -0.01502 | 134.2341 | -0.00054498 | -0.045061 | 6.7117 | -0.0016349 | 6.665 |  | 10.665 | 4 | 10.665 | 41.6563 | 20.8282 | 20 | 20 | 0.82815 | 23.8574
1007 | 16.7833 | 2.0049 | 10.4156 | 2 | 10.4 | 41.6414 | 0 | -0.01556 | 134.2185 | -0.00054015 | -0.046681 | 6.7109 | -0.0016204 | 6.6626 |  | 10.6626 | 4 | 10.6626 | 41.6414 | 20.8207 | 20 | 20 | 0.8207 | 24.6781
1008 | 16.8 | 2.005 | 10.4161 | 2 | 10.4 | 41.6264 | 0 | -0.016096 | 134.2025 | -0.00053529 | -0.048287 | 6.7101 | -0.0016059 | 6.6602 |  | 10.6602 | 4 | 10.6602 | 41.6264 | 20.8132 | 20 | 20 | 0.81322 | 25.4913
1009 | 16.8167 | 2.0052 | 10.4166 | 2 | 10.4 | 41.6114 | 0 | -0.016626 | 134.1858 | -0.0005304 | -0.049879 | 6.7093 | -0.0015912 | 6.6578 |  | 10.6578 | 4 | 10.6578 | 41.6114 | 20.8057 | 20 | 20 | 0.80569 | 26.297
1010 | 16.8333 | 2.0054 | 10.4172 | 2 | 10.4 | 41.5963 | 0 | -0.017152 | 134.1687 | -0.0005255 | -0.051455 | 6.7084 | -0.0015765 | 6.6554 |  | 10.6554 | 4 | 10.6554 | 41.5963 | 20.7981 | 20 | 20 | 0.79813 | 27.0951
1011 | 16.85 | 2.0055 | 10.4177 | 2 | 10.4 | 41.5811 | 0 | -0.017672 | 134.151 | -0.00052057 | -0.053017 | 6.7076 | -0.0015617 | 6.653 |  | 10.653 | 4 | 10.653 | 41.5811 | 20.7905 | 20 | 20 | 0.79054 | 27.8857
1012 | 16.8667 | 2.0057 | 10.4182 | 2 | 10.4 | 41.5658 | 0 | -0.018188 | 134.1328 | -0.00051561 | -0.054564 | 6.7066 | -0.0015468 | 6.6505 |  | 10.6505 | 4 | 10.6505 | 41.5658 | 20.7829 | 20 | 20 | 0.78291 | 28.6686
1013 | 16.8833 | 2.0058 | 10.4187 | 2 | 10.4 | 41.5505 | 0 | -0.018698 | 134.1141 | -0.00051064 | -0.056095 | 6.7057 | -0.0015319 | 6.6481 |  | 10.6481 | 4 | 10.6481 | 41.5505 | 20.7752 | 20 | 20 | 0.77525 | 29.4438
1014 | 16.9 | 2.006 | 10.4192 | 2 | 10.4 | 41.5351 | 0 | -0.019204 | 134.0949 | -0.00050564 | -0.057612 | 6.7047 | -0.0015169 | 6.6456 |  | 10.6456 | 4 | 10.6456 | 41.5351 | 20.7676 | 20 | 20 | 0.76755 | 30.2114
1015 | 16.9167 | 2.0062 | 10.4197 | 2 | 10.4 | 41.5197 | 0 | -0.019705 | 134.0752 | -0.00050062 | -0.059114 | 6.7038 | -0.0015019 | 6.6431 |  | 10.6431 | 4 | 10.6431 | 41.5197 | 20.7598 | 20 | 20 | 0.75983 | 30.9712
1016 | 16.9333 | 2.0063 | 10.4202 | 2 | 10.4 | 41.5041 | 0 | -0.0202 | 134.055 | -0.00049558 | -0.060601 | 6.7028 | -0.0014867 | 6.6407 |  | 10.6407 | 4 | 10.6407 | 41.5041 | 20.7521 | 20 | 20 | 0.75207 | 31.7233
1017 | 16.95 | 2.0065 | 10.4207 | 2 | 10.4 | 41.4886 | 0 | -0.020691 | 134.0343 | -0.00049052 | -0.062073 | 6.7017 | -0.0014716 | 6.6382 |  | 10.6382 | 4 | 10.6382 | 41.4886 | 20.7443 | 20 | 20 | 0.74429 | 32.4676
1018 | 16.9667 | 2.0066 | 10.4212 | 2 | 10.4 | 41.4729 | 0 | -0.021176 | 134.0131 | -0.00048545 | -0.063529 | 6.7007 | -0.0014563 | 6.6357 |  | 10.6357 | 4 | 10.6357 | 41.4729 | 20.7365 | 20 | 20 | 0.73647 | 33.204
1019 | 16.9833 | 2.0068 | 10.4217 | 2 | 10.4 | 41.4573 | 0 | -0.021657 | 133.9915 | -0.00048035 | -0.06497 | 6.6996 | -0.0014411 | 6.6332 |  | 10.6332 | 4 | 10.6332 | 41.4573 | 20.7286 | 20 | 20 | 0.72864 | 33.9327
1020 | 17 | 2.0069 | 10.4221 | 2 | 10.4 | 41.4415 | 0 | -0.022132 | 133.9694 | -0.00047524 | -0.066396 | 6.6985 | -0.0014257 | 6.6306 |  | 10.6306 | 4 | 10.6306 | 41.4415 | 20.7208 | 20 | 20 | 0.72077 | 34.6535
1021 | 17.0167 | 2.0071 | 10.4226 | 2 | 10.4 | 41.4258 | 0 | -0.022602 | 133.9468 | -0.00047011 | -0.067806 | 6.6973 | -0.0014103 | 6.6281 |  | 10.6281 | 4 | 10.6281 | 41.4258 | 20.7129 | 20 | 20 | 0.71288 | 35.3663
1022 | 17.0333 | 2.0072 | 10.4231 | 2 | 10.4 | 41.4099 | 0 | -0.023067 | 133.9237 | -0.00046496 | -0.069201 | 6.6962 | -0.0013949 | 6.6256 |  | 10.6256 | 4 | 10.6256 | 41.4099 | 20.705 | 20 | 20 | 0.70496 | 36.0713
1023 | 17.05 | 2.0074 | 10.4235 | 2 | 10.4 | 41.3941 | 0 | -0.023527 | 133.9002 | -0.0004598 | -0.07058 | 6.695 | -0.0013794 | 6.623 |  | 10.623 | 4 | 10.623 | 41.3941 | 20.697 | 20 | 20 | 0.69703 | 36.7683
1024 | 17.0667 | 2.0075 | 10.424 | 2 | 10.4 | 41.3781 | 0 | -0.023981 | 133.8762 | -0.00045462 | -0.071944 | 6.6938 | -0.0013639 | 6.6205 |  | 10.6205 | 4 | 10.6205 | 41.3781 | 20.6891 | 20 | 20 | 0.68907 | 37.4574
1025 | 17.0833 | 2.0076 | 10.4244 | 2 | 10.4 | 41.3622 | 0 | -0.024431 | 133.8517 | -0.00044943 | -0.073292 | 6.6926 | -0.0013483 | 6.6179 |  | 10.6179 | 4 | 10.6179 | 41.3622 | 20.6811 | 20 | 20 | 0.68108 | 38.1385
1026 | 17.1 | 2.0078 | 10.4249 | 2 | 10.4 | 41.3462 | 0 | -0.024875 | 133.8269 | -0.00044422 | -0.074625 | 6.6913 | -0.0013327 | 6.6154 |  | 10.6154 | 4 | 10.6154 | 41.3462 | 20.6731 | 20 | 20 | 0.67308 | 38.8115
1027 | 17.1167 | 2.0079 | 10.4253 | 2 | 10.4 | 41.3301 | 0 | -0.025314 | 133.8016 | -0.000439 | -0.075942 | 6.6901 | -0.001317 | 6.6128 |  | 10.6128 | 4 | 10.6128 | 41.3301 | 20.6651 | 20 | 20 | 0.66506 | 39.4766
1028 | 17.1333 | 2.008 | 10.4257 | 2 | 10.4 | 41.314 | 0 | -0.025748 | 133.7758 | -0.00043377 | -0.077243 | 6.6888 | -0.0013013 | 6.6102 |  | 10.6102 | 4 | 10.6102 | 41.314 | 20.657 | 20 | 20 | 0.65702 | 40.1336
1029 | 17.15 | 2.0082 | 10.4262 | 2 | 10.4 | 41.2979 | 0 | -0.026176 | 133.7496 | -0.00042853 | -0.078529 | 6.6875 | -0.0012856 | 6.6077 |  | 10.6077 | 4 | 10.6077 | 41.2979 | 20.649 | 20 | 20 | 0.64896 | 40.7826
1030 | 17.1667 | 2.0083 | 10.4266 | 2 | 10.4 | 41.2818 | 0 | -0.0266 | 133.723 | -0.00042327 | -0.079799 | 6.6862 | -0.0012698 | 6.6051 |  | 10.6051 | 4 | 10.6051 | 41.2818 | 20.6409 | 20 | 20 | 0.64088 | 41.4235
1031 | 17.1833 | 2.0084 | 10.427 | 2 | 10.4 | 41.2656 | 0 | -0.027018 | 133.696 | -0.000418 | -0.081053 | 6.6848 | -0.001254 | 6.6025 |  | 10.6025 | 4 | 10.6025 | 41.2656 | 20.6328 | 20 | 20 | 0.63279 | 42.0563
1032 | 17.2 | 2.0086 | 10.4274 | 2 | 10.4 | 41.2494 | 0 | -0.02743 | 133.6686 | -0.00041273 | -0.082291 | 6.6834 | -0.0012382 | 6.5999 |  | 10.5999 | 4 | 10.5999 | 41.2494 | 20.6247 | 20 | 20 | 0.62469 | 42.6809
1033 | 17.2167 | 2.0087 | 10.4278 | 2 | 10.4 | 41.2331 | 0 | -0.027838 | 133.6407 | -0.00040744 | -0.083513 | 6.682 | -0.0012223 | 6.5973 |  | 10.5973 | 4 | 10.5973 | 41.2331 | 20.6166 | 20 | 20 | 0.61657 | 43.2975
1034 | 17.2333 | 2.0088 | 10.4282 | 2 | 10.4 | 41.2169 | 0 | -0.02824 | 133.6125 | -0.00040214 | -0.08472 | 6.6806 | -0.0012064 | 6.5947 |  | 10.5947 | 4 | 10.5947 | 41.2169 | 20.6084 | 20 | 20 | 0.60843 | 43.906
1035 | 17.25 | 2.0089 | 10.4286 | 2 | 10.4 | 41.2006 | 0 | -0.028637 | 133.5839 | -0.00039684 | -0.08591 | 6.6792 | -0.0011905 | 6.5921 |  | 10.5921 | 4 | 10.5921 | 41.2006 | 20.6003 | 20 | 20 | 0.60029 | 44.5062
1036 | 17.2667 | 2.0091 | 10.429 | 2 | 10.4 | 41.1843 | 0 | -0.029028 | 133.5548 | -0.00039153 | -0.087085 | 6.6777 | -0.0011746 | 6.5895 |  | 10.5895 | 4 | 10.5895 | 41.1843 | 20.5921 | 20 | 20 | 0.59213 | 45.0984
1037 | 17.2833 | 2.0092 | 10.4294 | 2 | 10.4 | 41.1679 | 0 | -0.029414 | 133.5254 | -0.00038621 | -0.088243 | 6.6763 | -0.0011586 | 6.5869 |  | 10.5869 | 4 | 10.5869 | 41.1679 | 20.584 | 20 | 20 | 0.58397 | 45.6823
1038 | 17.3 | 2.0093 | 10.4298 | 2 | 10.4 | 41.1516 | 0 | -0.029795 | 133.4956 | -0.00038088 | -0.089386 | 6.6748 | -0.0011426 | 6.5843 |  | 10.5843 | 4 | 10.5843 | 41.1516 | 20.5758 | 20 | 20 | 0.57579 | 46.2581
1039 | 17.3167 | 2.0094 | 10.4302 | 2 | 10.4 | 41.1352 | 0 | -0.030171 | 133.4655 | -0.00037555 | -0.090513 | 6.6733 | -0.0011266 | 6.5816 |  | 10.5816 | 4 | 10.5816 | 41.1352 | 20.5676 | 20 | 20 | 0.56761 | 46.8257
1040 | 17.3333 | 2.0095 | 10.4305 | 2 | 10.4 | 41.1188 | 0 | -0.030541 | 133.4349 | -0.00037021 | -0.091623 | 6.6717 | -0.0011106 | 6.579 |  | 10.579 | 4 | 10.579 | 41.1188 | 20.5594 | 20 | 20 | 0.55941 | 47.3851
1041 | 17.35 | 2.0097 | 10.4309 | 2 | 10.4 | 41.1024 | 0 | -0.030906 | 133.404 | -0.00036487 | -0.092718 | 6.6702 | -0.0010946 | 6.5764 |  | 10.5764 | 4 | 10.5764 | 41.1024 | 20.5512 | 20 | 20 | 0.55121 | 47.9364
1042 | 17.3667 | 2.0098 | 10.4313 | 2 | 10.4 | 41.086 | 0 | -0.031265 | 133.3727 | -0.00035952 | -0.093796 | 6.6686 | -0.0010786 | 6.5738 |  | 10.5738 | 4 | 10.5738 | 41.086 | 20.543 | 20 | 20 | 0.54301 | 48.4794
1043 | 17.3833 | 2.0099 | 10.4316 | 2 | 10.4 | 41.0696 | 0 | -0.03162 | 133.3411 | -0.00035417 | -0.094859 | 6.6671 | -0.0010625 | 6.5711 |  | 10.5711 | 4 | 10.5711 | 41.0696 | 20.5348 | 20 | 20 | 0.5348 | 49.0142
1044 | 17.4 | 2.01 | 10.432 | 2 | 10.4 | 41.0532 | 0 | -0.031968 | 133.3092 | -0.00034881 | -0.095905 | 6.6655 | -0.0010464 | 6.5685 |  | 10.5685 | 4 | 10.5685 | 41.0532 | 20.5266 | 20 | 20 | 0.52658 | 49.5407
1045 | 17.4167 | 2.0101 | 10.4323 | 2 | 10.4 | 41.0367 | 0 | -0.032312 | 133.2768 | -0.00034345 | -0.096936 | 6.6638 | -0.0010304 | 6.5659 |  | 10.5659 | 4 | 10.5659 | 41.0367 | 20.5184 | 20 | 20 | 0.51836 | 50.0591
1046 | 17.4333 | 2.0102 | 10.4327 | 2 | 10.4 | 41.0203 | 0 | -0.03265 | 133.2442 | -0.00033809 | -0.09795 | 6.6622 | -0.0010143 | 6.5632 |  | 10.5632 | 4 | 10.5632 | 41.0203 | 20.5101 | 20 | 20 | 0.51014 | 50.5693
1047 | 17.45 | 2.0103 | 10.433 | 2 | 10.4 | 41.0038 | 0 | -0.032983 | 133.2112 | -0.00033273 | -0.098948 | 6.6606 | -0.00099819 | 6.5606 |  | 10.5606 | 4 | 10.5606 | 41.0038 | 20.5019 | 20 | 20 | 0.50192 | 51.0712
1048 | 17.4667 | 2.0104 | 10.4333 | 2 | 10.4 | 40.9874 | 0 | -0.03331 | 133.1779 | -0.00032737 | -0.09993 | 6.6589 | -0.0009821 | 6.558 |  | 10.558 | 4 | 10.558 | 40.9874 | 20.4937 | 20 | 20 | 0.4937 | 51.5649
1049 | 17.4833 | 2.0105 | 10.4336 | 2 | 10.4 | 40.9709 | 0 | -0.033632 | 133.1443 | -0.000322 | -0.1009 | 6.6572 | -0.00096601 | 6.5554 |  | 10.5554 | 4 | 10.5554 | 40.9709 | 20.4855 | 20 | 20 | 0.48547 | 52.0503
1050 | 17.5 | 2.0106 | 10.4339 | 2 | 10.4 | 40.9545 | 0 | -0.033949 | 133.1103 | -0.00031664 | -0.10185 | 6.6555 | -0.00094992 | 6.5527 |  | 10.5527 | 4 | 10.5527 | 40.9545 | 20.4773 | 20 | 20 | 0.47725 | 52.5276
1051 | 17.5167 | 2.0107 | 10.4343 | 2 | 10.4 | 40.9381 | 0 | -0.03426 | 133.0761 | -0.00031128 | -0.10278 | 6.6538 | -0.00093383 | 6.5501 |  | 10.5501 | 4 | 10.5501 | 40.9381 | 20.469 | 20 | 20 | 0.46903 | 52.9966
1052 | 17.5333 | 2.0108 | 10.4346 | 2 | 10.4 | 40.9216 | 0 | -0.034566 | 133.0415 | -0.00030591 | -0.1037 | 6.6521 | -0.00091774 | 6.5475 |  | 10.5475 | 4 | 10.5475 | 40.9216 | 20.4608 | 20 | 20 | 0.46081 | 53.4574
1053 | 17.55 | 2.0109 | 10.4349 | 2 | 10.4 | 40.9052 | 0 | -0.034867 | 133.0066 | -0.00030055 | -0.1046 | 6.6503 | -0.00090166 | 6.5448 |  | 10.5448 | 4 | 10.5448 | 40.9052 | 20.4526 | 20 | 20 | 0.4526 | 53.91
1054 | 17.5667 | 2.011 | 10.4352 | 2 | 10.4 | 40.8888 | 0 | -0.035162 | 132.9715 | -0.0002952 | -0.10549 | 6.6486 | -0.00088559 | 6.5422 |  | 10.5422 | 4 | 10.5422 | 40.8888 | 20.4444 | 20 | 20 | 0.44438 | 54.3544
1055 | 17.5833 | 2.0111 | 10.4355 | 2 | 10.4 | 40.8724 | 0 | -0.035452 | 132.936 | -0.00028984 | -0.10635 | 6.6468 | -0.00086952 | 6.5396 |  | 10.5396 | 4 | 10.5396 | 40.8724 | 20.4362 | 20 | 20 | 0.43618 | 54.7906
1056 | 17.6 | 2.0112 | 10.4357 | 2 | 10.4 | 40.856 | 0 | -0.035736 | 132.9003 | -0.00028449 | -0.10721 | 6.645 | -0.00085346 | 6.537 |  | 10.537 | 4 | 10.537 | 40.856 | 20.428 | 20 | 20 | 0.42798 | 55.2186
1057 | 17.6167 | 2.0113 | 10.436 | 2 | 10.4 | 40.8396 | 0 | -0.036015 | 132.8643 | -0.00027914 | -0.10805 | 6.6432 | -0.00083742 | 6.5343 |  | 10.5343 | 4 | 10.5343 | 40.8396 | 20.4198 | 20 | 20 | 0.41978 | 55.6383
1058 | 17.6333 | 2.0113 | 10.4363 | 2 | 10.4 | 40.8232 | 0 | -0.036289 | 132.828 | -0.00027379 | -0.10887 | 6.6414 | -0.00082138 | 6.5317 |  | 10.5317 | 4 | 10.5317 | 40.8232 | 20.4116 | 20 | 20 | 0.4116 | 56.0499
1059 | 17.65 | 2.0114 | 10.4366 | 2 | 10.4 | 40.8068 | 0 | -0.036557 | 132.7914 | -0.00026845 | -0.10967 | 6.6396 | -0.00080536 | 6.5291 |  | 10.5291 | 4 | 10.5291 | 40.8068 | 20.4034 | 20 | 20 | 0.40342 | 56.4534
1060 | 17.6667 | 2.0115 | 10.4368 | 2 | 10.4 | 40.7905 | 0 | -0.036821 | 132.7546 | -0.00026312 | -0.11046 | 6.6377 | -0.00078936 | 6.5265 |  | 10.5265 | 4 | 10.5265 | 40.7905 | 20.3952 | 20 | 20 | 0.39525 | 56.8486
1061 | 17.6833 | 2.0116 | 10.4371 | 2 | 10.4 | 40.7742 | 0 | -0.037078 | 132.7175 | -0.00025779 | -0.11123 | 6.6359 | -0.00077338 | 6.5239 |  | 10.5239 | 4 | 10.5239 | 40.7742 | 20.3871 | 20 | 20 | 0.38709 | 57.2357
1062 | 17.7 | 2.0117 | 10.4373 | 2 | 10.4 | 40.7579 | 0 | -0.037331 | 132.6802 | -0.00025247 | -0.11199 | 6.634 | -0.00075741 | 6.5213 |  | 10.5213 | 4 | 10.5213 | 40.7579 | 20.3789 | 20 | 20 | 0.37894 | 57.6146
1063 | 17.7167 | 2.0117 | 10.4376 | 2 | 10.4 | 40.7416 | 0 | -0.037578 | 132.6426 | -0.00024715 | -0.11273 | 6.6321 | -0.00074146 | 6.5187 |  | 10.5187 | 4 | 10.5187 | 40.7416 | 20.3708 | 20 | 20 | 0.3708 | 57.9854
1064 | 17.7333 | 2.0118 | 10.4378 | 2 | 10.4 | 40.7253 | 0 | -0.03782 | 132.6048 | -0.00024185 | -0.11346 | 6.6302 | -0.00072554 | 6.5161 |  | 10.5161 | 4 | 10.5161 | 40.7253 | 20.3627 | 20 | 20 | 0.36267 | 58.3481
1065 | 17.75 | 2.0119 | 10.4381 | 2 | 10.4 | 40.7091 | 0 | -0.038056 | 132.5667 | -0.00023654 | -0.11417 | 6.6283 | -0.00070963 | 6.5135 |  | 10.5135 | 4 | 10.5135 | 40.7091 | 20.3546 | 20 | 20 | 0.35456 | 58.7027
1066 | 17.7667 | 2.012 | 10.4383 | 2 | 10.4 | 40.6929 | 0 | -0.038288 | 132.5284 | -0.00023125 | -0.11486 | 6.6264 | -0.00069376 | 6.5109 |  | 10.5109 | 4 | 10.5109 | 40.6929 | 20.3465 | 20 | 20 | 0.34646 | 59.0491
1067 | 17.7833 | 2.012 | 10.4385 | 2 | 10.4 | 40.6767 | 0 | -0.038514 | 132.4899 | -0.00022597 | -0.11554 | 6.6245 | -0.00067791 | 6.5083 |  | 10.5083 | 4 | 10.5083 | 40.6767 | 20.3384 | 20 | 20 | 0.33837 | 59.3875
1068 | 17.8 | 2.0121 | 10.4387 | 2 | 10.4 | 40.6606 | 0 | -0.038734 | 132.4512 | -0.00022069 | -0.1162 | 6.6226 | -0.00066208 | 6.5057 |  | 10.5057 | 4 | 10.5057 | 40.6606 | 20.3303 | 20 | 20 | 0.3303 | 59.7178
1069 | 17.8167 | 2.0122 | 10.4389 | 2 | 10.4 | 40.6445 | 0 | -0.03895 | 132.4123 | -0.00021543 | -0.11685 | 6.6206 | -0.00064629 | 6.5031 |  | 10.5031 | 4 | 10.5031 | 40.6445 | 20.3222 | 20 | 20 | 0.32224 | 60.04
1070 | 17.8333 | 2.0122 | 10.4392 | 2 | 10.4 | 40.6284 | 0 | -0.03916 | 132.3731 | -0.00021018 | -0.11748 | 6.6187 | -0.00063053 | 6.5005 |  | 10.5005 | 4 | 10.5005 | 40.6284 | 20.3142 | 20 | 20 | 0.3142 | 60.3542
1071 | 17.85 | 2.0123 | 10.4394 | 2 | 10.4 | 40.6124 | 0 | -0.039365 | 132.3337 | -0.00020493 | -0.11809 | 6.6167 | -0.00061479 | 6.498 |  | 10.498 | 4 | 10.498 | 40.6124 | 20.3062 | 20 | 20 | 0.30618 | 60.6604
1072 | 17.8667 | 2.0124 | 10.4396 | 2 | 10.4 | 40.5963 | 0 | -0.039564 | 132.2942 | -0.0001997 | -0.11869 | 6.6147 | -0.0005991 | 6.4954 |  | 10.4954 | 4 | 10.4954 | 40.5963 | 20.2982 | 20 | 20 | 0.29817 | 60.9586
1073 | 17.8833 | 2.0124 | 10.4398 | 2 | 10.4 | 40.5804 | 0 | -0.039759 | 132.2544 | -0.00019448 | -0.11928 | 6.6127 | -0.00058343 | 6.4929 |  | 10.4929 | 4 | 10.4929 | 40.5804 | 20.2902 | 20 | 20 | 0.29019 | 61.2488
1074 | 17.9 | 2.0125 | 10.4399 | 2 | 10.4 | 40.5644 | 0 | -0.039948 | 132.2145 | -0.00018927 | -0.11984 | 6.6107 | -0.00056781 | 6.4903 |  | 10.4903 | 4 | 10.4903 | 40.5644 | 20.2822 | 20 | 20 | 0.28222 | 61.531
1075 | 17.9167 | 2.0125 | 10.4401 | 2 | 10.4 | 40.5485 | 0 | -0.040132 | 132.1743 | -0.00018407 | -0.1204 | 6.6087 | -0.00055222 | 6.4878 |  | 10.4878 | 4 | 10.4878 | 40.5485 | 20.2743 | 20 | 20 | 0.27427 | 61.8053
1076 | 17.9333 | 2.0126 | 10.4403 | 2 | 10.4 | 40.5327 | 0 | -0.040311 | 132.134 | -0.00017889 | -0.12093 | 6.6067 | -0.00053666 | 6.4852 |  | 10.4852 | 4 | 10.4852 | 40.5327 | 20.2663 | 20 | 20 | 0.26634 | 62.0716
1077 | 17.95 | 2.0127 | 10.4405 | 2 | 10.4 | 40.5169 | 0 | -0.040485 | 132.0935 | -0.00017372 | -0.12145 | 6.6047 | -0.00052115 | 6.4827 |  | 10.4827 | 4 | 10.4827 | 40.5169 | 20.2584 | 20 | 20 | 0.25844 | 62.33
1078 | 17.9667 | 2.0127 | 10.4407 | 2 | 10.4 | 40.5011 | 0 | -0.040653 | 132.0529 | -0.00016856 | -0.12196 | 6.6026 | -0.00050568 | 6.4802 |  | 10.4802 | 4 | 10.4802 | 40.5011 | 20.2506 | 20 | 20 | 0.25055 | 62.5806
1079 | 17.9833 | 2.0128 | 10.4408 | 2 | 10.4 | 40.4854 | 0 | -0.040817 | 132.0121 | -0.00016342 | -0.12245 | 6.6006 | -0.00049026 | 6.4777 |  | 10.4777 | 4 | 10.4777 | 40.4854 | 20.2427 | 20 | 20 | 0.24269 | 62.8233
1080 | 18 | 2.0128 | 10.441 | 2 | 10.4 | 40.4697 | 0 | -0.040975 | 131.9711 | -0.00015829 | -0.12293 | 6.5986 | -0.00047488 | 6.4752 |  | 10.4752 | 4 | 10.4752 | 40.4697 | 20.2349 | 20 | 20 | 0.23486 | 63.0581
1081 | 18.0167 | 2.0129 | 10.4411 | 2 | 10.4 | 40.4541 | 0 | -0.041128 | 131.93 | -0.00015318 | -0.12339 | 6.5965 | -0.00045954 | 6.4727 |  | 10.4727 | 4 | 10.4727 | 40.4541 | 20.227 | 20 | 20 | 0.22704 | 63.2852
1082 | 18.0333 | 2.0129 | 10.4413 | 2 | 10.4 | 40.4385 | 0 | -0.041276 | 131.8887 | -0.00014808 | -0.12383 | 6.5944 | -0.00044425 | 6.4702 |  | 10.4702 | 4 | 10.4702 | 40.4385 | 20.2193 | 20 | 20 | 0.21925 | 63.5044
1083 | 18.05 | 2.0129 | 10.4414 | 2 | 10.4 | 40.423 | 0 | -0.041419 | 131.8473 | -0.000143 | -0.12426 | 6.5924 | -0.00042901 | 6.4677 |  | 10.4677 | 4 | 10.4677 | 40.423 | 20.2115 | 20 | 20 | 0.21149 | 63.7159
1084 | 18.0667 | 2.013 | 10.4416 | 2 | 10.4 | 40.4075 | 0 | -0.041557 | 131.8057 | -0.00013794 | -0.12467 | 6.5903 | -0.00041381 | 6.4652 |  | 10.4652 | 4 | 10.4652 | 40.4075 | 20.2037 | 20 | 20 | 0.20375 | 63.9197
1085 | 18.0833 | 2.013 | 10.4417 | 2 | 10.4 | 40.3921 | 0 | -0.04169 | 131.764 | -0.00013289 | -0.12507 | 6.5882 | -0.00039867 | 6.4627 |  | 10.4627 | 4 | 10.4627 | 40.3921 | 20.196 | 20 | 20 | 0.19603 | 64.1157
1086 | 18.1 | 2.0131 | 10.4418 | 2 | 10.4 | 40.3767 | 0 | -0.041818 | 131.7222 | -0.00012786 | -0.12545 | 6.5861 | -0.00038358 | 6.4603 |  | 10.4603 | 4 | 10.4603 | 40.3767 | 20.1883 | 20 | 20 | 0.18835 | 64.304
1087 | 18.1167 | 2.0131 | 10.4419 | 2 | 10.4 | 40.3614 | 0 | -0.041941 | 131.6803 | -0.00012285 | -0.12582 | 6.584 | -0.00036854 | 6.4578 |  | 10.4578 | 4 | 10.4578 | 40.3614 | 20.1807 | 20 | 20 | 0.18069 | 64.4847
1088 | 18.1333 | 2.0131 | 10.4421 | 2 | 10.4 | 40.3461 | 0 | -0.042059 | 131.6382 | -0.00011785 | -0.12618 | 6.5819 | -0.00035356 | 6.4554 |  | 10.4554 | 4 | 10.4554 | 40.3461 | 20.1731 | 20 | 20 | 0.17306 | 64.6578
1089 | 18.15 | 2.0132 | 10.4422 | 2 | 10.4 | 40.3309 | 0 | -0.042172 | 131.596 | -0.00011288 | -0.12652 | 6.5798 | -0.00033863 | 6.4529 |  | 10.4529 | 4 | 10.4529 | 40.3309 | 20.1655 | 20 | 20 | 0.16546 | 64.8233
1090 | 18.1667 | 2.0132 | 10.4423 | 2 | 10.4 | 40.3158 | 0 | -0.04228 | 131.5537 | -0.00010792 | -0.12684 | 6.5777 | -0.00032375 | 6.4505 |  | 10.4505 | 4 | 10.4505 | 40.3158 | 20.1579 | 20 | 20 | 0.15789 | 64.9811
1091 | 18.1833 | 2.0132 | 10.4424 | 2 | 10.4 | 40.3007 | 0 | -0.042383 | 131.5114 | -0.00010298 | -0.12715 | 6.5756 | -0.00030894 | 6.4481 |  | 10.4481 | 4 | 10.4481 | 40.3007 | 20.1503 | 20 | 20 | 0.15035 | 65.1315
1092 | 18.2 | 2.0133 | 10.4425 | 2 | 10.4 | 40.2857 | 0 | -0.042481 | 131.4689 | -9.8061e-05 | -0.12744 | 6.5734 | -0.00029418 | 6.4457 |  | 10.4457 | 4 | 10.4457 | 40.2857 | 20.1428 | 20 | 20 | 0.14284 | 65.2743
1093 | 18.2167 | 2.0133 | 10.4426 | 2 | 10.4 | 40.2707 | 0 | -0.042574 | 131.4263 | -9.3162e-05 | -0.12772 | 6.5713 | -0.00027949 | 6.4433 |  | 10.4433 | 4 | 10.4433 | 40.2707 | 20.1354 | 20 | 20 | 0.13536 | 65.4097
1094 | 18.2333 | 2.0133 | 10.4427 | 2 | 10.4 | 40.2558 | 0 | -0.042662 | 131.3836 | -8.8284e-05 | -0.12799 | 6.5692 | -0.00026485 | 6.4409 |  | 10.4409 | 4 | 10.4409 | 40.2558 | 20.1279 | 20 | 20 | 0.12791 | 65.5376
1095 | 18.25 | 2.0134 | 10.4427 | 2 | 10.4 | 40.241 | 0 | -0.042746 | 131.3409 | -8.3426e-05 | -0.12824 | 6.567 | -0.00025028 | 6.4386 |  | 10.4386 | 4 | 10.4386 | 40.241 | 20.1205 | 20 | 20 | 0.12049 | 65.6581
1096 | 18.2667 | 2.0134 | 10.4428 | 2 | 10.4 | 40.2262 | 0 | -0.042824 | 131.2981 | -7.8589e-05 | -0.12847 | 6.5649 | -0.00023577 | 6.4362 |  | 10.4362 | 4 | 10.4362 | 40.2262 | 20.1131 | 20 | 20 | 0.11311 | 65.7712
1097 | 18.2833 | 2.0134 | 10.4429 | 2 | 10.4 | 40.2115 | 0 | -0.042898 | 131.2552 | -7.3774e-05 | -0.12869 | 6.5628 | -0.00022132 | 6.4338 |  | 10.4338 | 4 | 10.4338 | 40.2115 | 20.1058 | 20 | 20 | 0.10576 | 65.877
1098 | 18.3 | 2.0134 | 10.443 | 2 | 10.4 | 40.1969 | 0 | -0.042967 | 131.2122 | -6.8981e-05 | -0.1289 | 6.5606 | -0.00020694 | 6.4315 |  | 10.4315 | 4 | 10.4315 | 40.1969 | 20.0984 | 20 | 20 | 0.098446 | 65.9754
1099 | 18.3167 | 2.0134 | 10.443 | 2 | 10.4 | 40.1823 | 0 | -0.043031 | 131.1692 | -6.4209e-05 | -0.12909 | 6.5585 | -0.00019263 | 6.4292 |  | 10.4292 | 4 | 10.4292 | 40.1823 | 20.0912 | 20 | 20 | 0.091165 | 66.0666
1100 | 18.3333 | 2.0135 | 10.4431 | 2 | 10.4 | 40.1678 | 0 | -0.043091 | 131.1261 | -5.9461e-05 | -0.12927 | 6.5563 | -0.00017838 | 6.4269 |  | 10.4269 | 4 | 10.4269 | 40.1678 | 20.0839 | 20 | 20 | 0.083919 | 66.1505
1101 | 18.35 | 2.0135 | 10.4431 | 2 | 10.4 | 40.1534 | 0 | -0.043145 | 131.0829 | -5.4735e-05 | -0.12944 | 6.5541 | -0.0001642 | 6.4245 |  | 10.4245 | 4 | 10.4245 | 40.1534 | 20.0767 | 20 | 20 | 0.076709 | 66.2272
1102 | 18.3667 | 2.0135 | 10.4432 | 2 | 10.4 | 40.1391 | 0 | -0.043195 | 131.0397 | -5.0032e-05 | -0.12959 | 6.552 | -0.0001501 | 6.4223 |  | 10.4223 | 4 | 10.4223 | 40.1391 | 20.0695 | 20 | 20 | 0.069535 | 66.2967
1103 | 18.3833 | 2.0135 | 10.4432 | 2 | 10.4 | 40.1248 | 0 | -0.043241 | 130.9965 | -4.5353e-05 | -0.12972 | 6.5498 | -0.00013606 | 6.42 |  | 10.42 | 4 | 10.42 | 40.1248 | 20.0624 | 20 | 20 | 0.062397 | 66.3591
1104 | 18.4 | 2.0135 | 10.4433 | 2 | 10.4 | 40.1106 | 0 | -0.043281 | 130.9532 | -4.0697e-05 | -0.12984 | 6.5477 | -0.00012209 | 6.4177 |  | 10.4177 | 4 | 10.4177 | 40.1106 | 20.0553 | 20 | 20 | 0.055297 | 66.4144
1105 | 18.4167 | 2.0135 | 10.4433 | 2 | 10.4 | 40.0965 | 0 | -0.043317 | 130.9099 | -3.6066e-05 | -0.12995 | 6.5455 | -0.0001082 | 6.4154 |  | 10.4154 | 4 | 10.4154 | 40.0965 | 20.0482 | 20 | 20 | 0.048234 | 66.4627
1106 | 18.4333 | 2.0135 | 10.4433 | 2 | 10.4 | 40.0824 | 0 | -0.043349 | 130.8666 | -3.1459e-05 | -0.13005 | 6.5433 | -9.4378e-05 | 6.4132 |  | 10.4132 | 4 | 10.4132 | 40.0824 | 20.0412 | 20 | 20 | 0.041209 | 66.5039
1107 | 18.45 | 2.0136 | 10.4434 | 2 | 10.4 | 40.0684 | 0 | -0.043376 | 130.8232 | -2.6877e-05 | -0.13013 | 6.5412 | -8.0632e-05 | 6.411 |  | 10.411 | 4 | 10.411 | 40.0684 | 20.0342 | 20 | 20 | 0.034222 | 66.5381
1108 | 18.4667 | 2.0136 | 10.4434 | 2 | 10.4 | 40.0545 | 0 | -0.043398 | 130.7798 | -2.2321e-05 | -0.13019 | 6.539 | -6.6962e-05 | 6.4087 |  | 10.4087 | 4 | 10.4087 | 40.0545 | 20.0273 | 20 | 20 | 0.027275 | 66.5654
1109 | 18.4833 | 2.0136 | 10.4434 | 2 | 10.4 | 40.0407 | 0 | -0.043416 | 130.7364 | -1.7789e-05 | -0.13025 | 6.5368 | -5.3368e-05 | 6.4065 |  | 10.4065 | 4 | 10.4065 | 40.0407 | 20.0204 | 20 | 20 | 0.020367 | 66.5857
1110 | 18.5 | 2.0136 | 10.4434 | 2 | 10.4 | 40.027 | 0 | -0.043429 | 130.6929 | -1.3284e-05 | -0.13029 | 6.5346 | -3.9851e-05 | 6.4043 |  | 10.4043 | 4 | 10.4043 | 40.027 | 20.0135 | 20 | 20 | 0.013498 | 66.5992
1111 | 18.5167 | 2.0136 | 10.4434 | 2 | 10.4 | 40.0133 | 0 | -0.043438 | 130.6495 | -8.8041e-06 | -0.13031 | 6.5325 | -2.6412e-05 | 6.4021 |  | 10.4021 | 4 | 10.4021 | 40.0133 | 20.0067 | 20 | 20 | 0.0066707 | 66.6059
1112 | 18.5333 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9998 | 0 | -0.043442 | 130.6061 | -4.3508e-06 | -0.13033 | 6.5303 | -1.3053e-05 | 6.4 |  | 10.4 | 4 | 10.4 | 39.9998 | 19.9999 | 20 | 20 | -0.00011617 | 66.6058
1113 | 18.55 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9863 | 0 | -0.043442 | 130.5626 | 7.5769e-08 | -0.13033 | 6.5281 | 2.2731e-07 | 6.3978 |  | 10.3978 | 4 | 10.3978 | 39.9863 | 19.9931 | 20 | 20 | -0.0068618 | 66.5989
1114 | 18.5667 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9729 | 0 | -0.043438 | 130.5192 | 4.4755e-06 | -0.13031 | 6.526 | 1.3426e-05 | 6.3957 |  | 10.3957 | 4 | 10.3957 | 39.9729 | 19.9864 | 20 | 20 | -0.013566 | 66.5854
1115 | 18.5833 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9595 | 0 | -0.043429 | 130.4757 | 8.848e-06 | -0.13029 | 6.5238 | 2.6544e-05 | 6.3935 |  | 10.3935 | 4 | 10.3935 | 39.9595 | 19.9798 | 20 | 20 | -0.020228 | 66.5651
1116 | 18.6 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9463 | 0 | -0.043416 | 130.4323 | 1.3193e-05 | -0.13025 | 6.5216 | 3.9579e-05 | 6.3914 |  | 10.3914 | 4 | 10.3914 | 39.9463 | 19.9732 | 20 | 20 | -0.026847 | 66.5383
1117 | 18.6167 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9332 | 0 | -0.043398 | 130.3889 | 1.751e-05 | -0.13019 | 6.5194 | 5.2531e-05 | 6.3893 |  | 10.3893 | 4 | 10.3893 | 39.9332 | 19.9666 | 20 | 20 | -0.033423 | 66.5049
1118 | 18.6333 | 2.0136 | 10.4434 | 2 | 10.4 | 39.9201 | 0 | -0.043376 | 130.3456 | 2.18e-05 | -0.13013 | 6.5173 | 6.5399e-05 | 6.3872 |  | 10.3872 | 4 | 10.3872 | 39.9201 | 19.96 | 20 | 20 | -0.039956 | 66.4649
1119 | 18.65 | 2.0135 | 10.4434 | 2 | 10.4 | 39.9071 | 0 | -0.04335 | 130.3022 | 2.6061e-05 | -0.13005 | 6.5151 | 7.8182e-05 | 6.3851 |  | 10.3851 | 4 | 10.3851 | 39.9071 | 19.9536 | 20 | 20 | -0.046445 | 66.4185
1120 | 18.6667 | 2.0135 | 10.4433 | 2 | 10.4 | 39.8942 | 0 | -0.04332 | 130.2589 | 3.0293e-05 | -0.12996 | 6.5129 | 9.0879e-05 | 6.3831 |  | 10.3831 | 4 | 10.3831 | 39.8942 | 19.9471 | 20 | 20 | -0.052891 | 66.3656
1121 | 18.6833 | 2.0135 | 10.4433 | 2 | 10.4 | 39.8814 | 0 | -0.043286 | 130.2156 | 3.4497e-05 | -0.12986 | 6.5108 | 0.00010349 | 6.381 |  | 10.381 | 4 | 10.381 | 39.8814 | 19.9407 | 20 | 20 | -0.059291 | 66.3063
1122 | 18.7 | 2.0135 | 10.4432 | 2 | 10.4 | 39.8687 | 0 | -0.043247 | 130.1724 | 3.8671e-05 | -0.12974 | 6.5086 | 0.00011601 | 6.379 |  | 10.379 | 4 | 10.379 | 39.8687 | 19.9344 | 20 | 20 | -0.065647 | 66.2406
1123 | 18.7167 | 2.0135 | 10.4432 | 2 | 10.4 | 39.8561 | 0 | -0.043204 | 130.1292 | 4.2817e-05 | -0.12961 | 6.5065 | 0.00012845 | 6.377 |  | 10.377 | 4 | 10.377 | 39.8561 | 19.928 | 20 | 20 | -0.071957 | 66.1687
1124 | 18.7333 | 2.0135 | 10.4432 | 2 | 10.4 | 39.8436 | 0 | -0.043157 | 130.086 | 4.6933e-05 | -0.12947 | 6.5043 | 0.0001408 | 6.375 |  | 10.375 | 4 | 10.375 | 39.8436 | 19.9218 | 20 | 20 | -0.078222 | 66.0905
1125 | 18.75 | 2.0135 | 10.4431 | 2 | 10.4 | 39.8311 | 0 | -0.043106 | 130.0429 | 5.1019e-05 | -0.12932 | 6.5021 | 0.00015306 | 6.373 |  | 10.373 | 4 | 10.373 | 39.8311 | 19.9156 | 20 | 20 | -0.084441 | 66.006
1126 | 18.7667 | 2.0135 | 10.4431 | 2 | 10.4 | 39.8188 | 0 | -0.043051 | 129.9998 | 5.5075e-05 | -0.12915 | 6.5 | 0.00016522 | 6.371 |  | 10.371 | 4 | 10.371 | 39.8188 | 19.9094 | 20 | 20 | -0.090613 | 65.9154
1127 | 18.7833 | 2.0134 | 10.443 | 2 | 10.4 | 39.8065 | 0 | -0.042992 | 129.9568 | 5.91e-05 | -0.12898 | 6.4978 | 0.0001773 | 6.369 |  | 10.369 | 4 | 10.369 | 39.8065 | 19.9033 | 20 | 20 | -0.096739 | 65.8187
1128 | 18.8 | 2.0134 | 10.4429 | 2 | 10.4 | 39.7944 | 0 | -0.042929 | 129.9139 | 6.3096e-05 | -0.12879 | 6.4957 | 0.00018929 | 6.3671 |  | 10.3671 | 4 | 10.3671 | 39.7944 | 19.8972 | 20 | 20 | -0.10282 | 65.7158
1129 | 18.8167 | 2.0134 | 10.4429 | 2 | 10.4 | 39.7823 | 0 | -0.042862 | 129.8711 | 6.706e-05 | -0.12859 | 6.4936 | 0.00020118 | 6.3652 |  | 10.3652 | 4 | 10.3652 | 39.7823 | 19.8912 | 20 | 20 | -0.10885 | 65.607
1130 | 18.8333 | 2.0134 | 10.4428 | 2 | 10.4 | 39.7703 | 0 | -0.042791 | 129.8283 | 7.0994e-05 | -0.12837 | 6.4914 | 0.00021298 | 6.3633 |  | 10.3633 | 4 | 10.3633 | 39.7703 | 19.8852 | 20 | 20 | -0.11483 | 65.4922
1131 | 18.85 | 2.0133 | 10.4427 | 2 | 10.4 | 39.7585 | 0 | -0.042716 | 129.7855 | 7.4897e-05 | -0.12815 | 6.4893 | 0.00022469 | 6.3614 |  | 10.3614 | 4 | 10.3614 | 39.7585 | 19.8792 | 20 | 20 | -0.12077 | 65.3714
1132 | 18.8667 | 2.0133 | 10.4426 | 2 | 10.4 | 39.7467 | 0 | -0.042637 | 129.7429 | 7.8768e-05 | -0.12791 | 6.4871 | 0.0002363 | 6.3595 |  | 10.3595 | 4 | 10.3595 | 39.7467 | 19.8733 | 20 | 20 | -0.12666 | 65.2447
1133 | 18.8833 | 2.0133 | 10.4426 | 2 | 10.4 | 39.735 | 0 | -0.042555 | 129.7004 | 8.2608e-05 | -0.12766 | 6.485 | 0.00024782 | 6.3576 |  | 10.3576 | 4 | 10.3576 | 39.735 | 19.8675 | 20 | 20 | -0.13249 | 65.1123
1134 | 18.9 | 2.0133 | 10.4425 | 2 | 10.4 | 39.7234 | 0 | -0.042468 | 129.6579 | 8.6416e-05 | -0.1274 | 6.4829 | 0.00025925 | 6.3557 |  | 10.3557 | 4 | 10.3557 | 39.7234 | 19.8617 | 20 | 20 | -0.13828 | 64.974
1135 | 18.9167 | 2.0132 | 10.4424 | 2 | 10.4 | 39.712 | 0 | -0.042378 | 129.6155 | 9.0193e-05 | -0.12713 | 6.4808 | 0.00027058 | 6.3539 |  | 10.3539 | 4 | 10.3539 | 39.712 | 19.856 | 20 | 20 | -0.14402 | 64.8299
1136 | 18.9333 | 2.0132 | 10.4423 | 2 | 10.4 | 39.7006 | 0 | -0.042284 | 129.5732 | 9.3937e-05 | -0.12685 | 6.4787 | 0.00028181 | 6.3521 |  | 10.3521 | 4 | 10.3521 | 39.7006 | 19.8503 | 20 | 20 | -0.14972 | 64.6802
1137 | 18.95 | 2.0132 | 10.4422 | 2 | 10.4 | 39.6893 | 0 | -0.042186 | 129.531 | 9.7649e-05 | -0.12656 | 6.4766 | 0.00029295 | 6.3503 |  | 10.3503 | 4 | 10.3503 | 39.6893 | 19.8446 | 20 | 20 | -0.15536 | 64.5249
1138 | 18.9667 | 2.0132 | 10.4421 | 2 | 10.4 | 39.6781 | 0 | -0.042085 | 129.489 | 0.00010133 | -0.12626 | 6.4744 | 0.00030398 | 6.3485 |  | 10.3485 | 4 | 10.3485 | 39.6781 | 19.8391 | 20 | 20 | -0.16095 | 64.3639
1139 | 18.9833 | 2.0131 | 10.442 | 2 | 10.4 | 39.667 | 0 | -0.04198 | 129.447 | 0.00010497 | -0.12594 | 6.4723 | 0.00031492 | 6.3467 |  | 10.3467 | 4 | 10.3467 | 39.667 | 19.8335 | 20 | 20 | -0.16649 | 64.1974
1140 | 19 | 2.0131 | 10.4419 | 2 | 10.4 | 39.656 | 0 | -0.041871 | 129.4051 | 0.00010859 | -0.12561 | 6.4703 | 0.00032577 | 6.345 |  | 10.345 | 4 | 10.345 | 39.656 | 19.828 | 20 | 20 | -0.17198 | 64.0255
1141 | 19.0167 | 2.013 | 10.4418 | 2 | 10.4 | 39.6452 | 0 | -0.041759 | 129.3633 | 0.00011217 | -0.12528 | 6.4682 | 0.00033651 | 6.3432 |  | 10.3432 | 4 | 10.3432 | 39.6452 | 19.8226 | 20 | 20 | -0.17742 | 63.848
1142 | 19.0333 | 2.013 | 10.4416 | 2 | 10.4 | 39.6344 | 0 | -0.041644 | 129.3217 | 0.00011572 | -0.12493 | 6.4661 | 0.00034715 | 6.3415 |  | 10.3415 | 4 | 10.3415 | 39.6344 | 19.8172 | 20 | 20 | -0.18281 | 63.6652
1143 | 19.05 | 2.013 | 10.4415 | 2 | 10.4 | 39.6237 | 0 | -0.041524 | 129.2802 | 0.00011923 | -0.12457 | 6.464 | 0.0003577 | 6.3398 |  | 10.3398 | 4 | 10.3398 | 39.6237 | 19.8119 | 20 | 20 | -0.18815 | 63.4771
1144 | 19.0667 | 2.0129 | 10.4414 | 2 | 10.4 | 39.6131 | 0 | -0.041402 | 129.2388 | 0.00012271 | -0.1242 | 6.4619 | 0.00036814 | 6.3381 |  | 10.3381 | 4 | 10.3381 | 39.6131 | 19.8066 | 20 | 20 | -0.19343 | 63.2837
1145 | 19.0833 | 2.0129 | 10.4413 | 2 | 10.4 | 39.6027 | 0 | -0.041275 | 129.1975 | 0.00012616 | -0.12383 | 6.4599 | 0.00037848 | 6.3364 |  | 10.3364 | 4 | 10.3364 | 39.6027 | 19.8013 | 20 | 20 | -0.19867 | 63.085
1146 | 19.1 | 2.0129 | 10.4411 | 2 | 10.4 | 39.5923 | 0 | -0.041146 | 129.1564 | 0.00012958 | -0.12344 | 6.4578 | 0.00038873 | 6.3348 |  | 10.3348 | 4 | 10.3348 | 39.5923 | 19.7962 | 20 | 20 | -0.20385 | 62.8811
1147 | 19.1167 | 2.0128 | 10.441 | 2 | 10.4 | 39.582 | 0 | -0.041013 | 129.1153 | 0.00013296 | -0.12304 | 6.4558 | 0.00039887 | 6.3331 |  | 10.3331 | 4 | 10.3331 | 39.582 | 19.791 | 20 | 20 | -0.20898 | 62.6722
1148 | 19.1333 | 2.0128 | 10.4409 | 2 | 10.4 | 39.5719 | 0 | -0.040877 | 129.0745 | 0.0001363 | -0.12263 | 6.4537 | 0.0004089 | 6.3315 |  | 10.3315 | 4 | 10.3315 | 39.5719 | 19.7859 | 20 | 20 | -0.21406 | 62.4581
1149 | 19.15 | 2.0127 | 10.4407 | 2 | 10.4 | 39.5618 | 0 | -0.040737 | 129.0337 | 0.00013961 | -0.12221 | 6.4517 | 0.00041884 | 6.3299 |  | 10.3299 | 4 | 10.3299 | 39.5618 | 19.7809 | 20 | 20 | -0.21908 | 62.239
1150 | 19.1667 | 2.0127 | 10.4406 | 2 | 10.4 | 39.5519 | 0 | -0.040594 | 128.9931 | 0.00014289 | -0.12178 | 6.4497 | 0.00042867 | 6.3283 |  | 10.3283 | 4 | 10.3283 | 39.5519 | 19.7759 | 20 | 20 | -0.22405 | 62.015
1151 | 19.1833 | 2.0126 | 10.4404 | 2 | 10.4 | 39.5421 | 0 | -0.040448 | 128.9527 | 0.00014613 | -0.12134 | 6.4476 | 0.0004384 | 6.3267 |  | 10.3267 | 4 | 10.3267 | 39.5421 | 19.771 | 20 | 20 | -0.22897 | 61.786
1152 | 19.2 | 2.0126 | 10.4403 | 2 | 10.4 | 39.5323 | 0 | -0.040299 | 128.9124 | 0.00014934 | -0.1209 | 6.4456 | 0.00044803 | 6.3252 |  | 10.3252 | 4 | 10.3252 | 39.5323 | 19.7662 | 20 | 20 | -0.23384 | 61.5522
1153 | 19.2167 | 2.0125 | 10.4401 | 2 | 10.4 | 39.5227 | 0 | -0.040146 | 128.8722 | 0.00015252 | -0.12044 | 6.4436 | 0.00045755 | 6.3236 |  | 10.3236 | 4 | 10.3236 | 39.5227 | 19.7613 | 20 | 20 | -0.23865 | 61.3135
1154 | 19.2333 | 2.0125 | 10.44 | 2 | 10.4 | 39.5132 | 0 | -0.03999 | 128.8322 | 0.00015566 | -0.11997 | 6.4416 | 0.00046697 | 6.3221 |  | 10.3221 | 4 | 10.3221 | 39.5132 | 19.7566 | 20 | 20 | -0.24341 | 61.0701
1155 | 19.25 | 2.0124 | 10.4398 | 2 | 10.4 | 39.5038 | 0 | -0.039832 | 128.7924 | 0.00015876 | -0.1195 | 6.4396 | 0.00047628 | 6.3206 |  | 10.3206 | 4 | 10.3206 | 39.5038 | 19.7519 | 20 | 20 | -0.24812 | 60.822
1156 | 19.2667 | 2.0124 | 10.4397 | 2 | 10.4 | 39.4945 | 0 | -0.03967 | 128.7527 | 0.00016183 | -0.11901 | 6.4376 | 0.00048549 | 6.3191 |  | 10.3191 | 4 | 10.3191 | 39.4945 | 19.7472 | 20 | 20 | -0.25277 | 60.5692
1157 | 19.2833 | 2.0123 | 10.4395 | 2 | 10.4 | 39.4853 | 0 | -0.039505 | 128.7132 | 0.00016486 | -0.11852 | 6.4357 | 0.00049459 | 6.3176 |  | 10.3176 | 4 | 10.3176 | 39.4853 | 19.7426 | 20 | 20 | -0.25737 | 60.3118
1158 | 19.3 | 2.0123 | 10.4393 | 2 | 10.4 | 39.4762 | 0 | -0.039337 | 128.6739 | 0.00016786 | -0.11801 | 6.4337 | 0.00050359 | 6.3162 |  | 10.3162 | 4 | 10.3162 | 39.4762 | 19.7381 | 20 | 20 | -0.26191 | 60.0499
1159 | 19.3167 | 2.0122 | 10.4392 | 2 | 10.4 | 39.4672 | 0 | -0.039166 | 128.6347 | 0.00017083 | -0.1175 | 6.4317 | 0.00051248 | 6.3148 |  | 10.3148 | 4 | 10.3148 | 39.4672 | 19.7336 | 20 | 20 | -0.2664 | 59.7835
1160 | 19.3333 | 2.0122 | 10.439 | 2 | 10.4 | 39.4583 | 0 | -0.038993 | 128.5957 | 0.00017376 | -0.11698 | 6.4298 | 0.00052127 | 6.3133 |  | 10.3133 | 4 | 10.3133 | 39.4583 | 19.7292 | 20 | 20 | -0.27084 | 59.5127
1161 | 19.35 | 2.0121 | 10.4388 | 2 | 10.4 | 39.4496 | 0 | -0.038816 | 128.5569 | 0.00017665 | -0.11645 | 6.4278 | 0.00052995 | 6.3119 |  | 10.3119 | 4 | 10.3119 | 39.4496 | 19.7248 | 20 | 20 | -0.27522 | 59.2375
1162 | 19.3667 | 2.0121 | 10.4386 | 2 | 10.4 | 39.4409 | 0 | -0.038636 | 128.5183 | 0.00017951 | -0.11591 | 6.4259 | 0.00053852 | 6.3105 |  | 10.3105 | 4 | 10.3105 | 39.4409 | 19.7205 | 20 | 20 | -0.27955 | 58.9579
1163 | 19.3833 | 2.012 | 10.4385 | 2 | 10.4 | 39.4324 | 0 | -0.038454 | 128.4798 | 0.00018233 | -0.11536 | 6.424 | 0.00054699 | 6.3092 |  | 10.3092 | 4 | 10.3092 | 39.4324 | 19.7162 | 20 | 20 | -0.28382 | 58.6741
1164 | 19.4 | 2.012 | 10.4383 | 2 | 10.4 | 39.4239 | 0 | -0.038269 | 128.4416 | 0.00018512 | -0.11481 | 6.4221 | 0.00055535 | 6.3078 |  | 10.3078 | 4 | 10.3078 | 39.4239 | 19.712 | 20 | 20 | -0.28804 | 58.386
1165 | 19.4167 | 2.0119 | 10.4381 | 2 | 10.4 | 39.4156 | 0 | -0.038081 | 128.4035 | 0.00018787 | -0.11424 | 6.4202 | 0.00056361 | 6.3065 |  | 10.3065 | 4 | 10.3065 | 39.4156 | 19.7078 | 20 | 20 | -0.2922 | 58.0938
1166 | 19.4333 | 2.0118 | 10.4379 | 2 | 10.4 | 39.4074 | 0 | -0.037891 | 128.3656 | 0.00019058 | -0.11367 | 6.4183 | 0.00057175 | 6.3052 |  | 10.3052 | 4 | 10.3052 | 39.4074 | 19.7037 | 20 | 20 | -0.29631 | 57.7975
1167 | 19.45 | 2.0118 | 10.4377 | 2 | 10.4 | 39.3993 | 0 | -0.037697 | 128.3279 | 0.00019326 | -0.11309 | 6.4164 | 0.00057979 | 6.3039 |  | 10.3039 | 4 | 10.3039 | 39.3993 | 19.6996 | 20 | 20 | -0.30037 | 57.4972
1168 | 19.4667 | 2.0117 | 10.4375 | 2 | 10.4 | 39.3913 | 0 | -0.037501 | 128.2904 | 0.00019591 | -0.1125 | 6.4145 | 0.00058772 | 6.3026 |  | 10.3026 | 4 | 10.3026 | 39.3913 | 19.6956 | 20 | 20 | -0.30436 | 57.1928
1169 | 19.4833 | 2.0117 | 10.4373 | 2 | 10.4 | 39.3834 | 0 | -0.037303 | 128.2531 | 0.00019851 | -0.11191 | 6.4127 | 0.00059554 | 6.3013 |  | 10.3013 | 4 | 10.3013 | 39.3834 | 19.6917 | 20 | 20 | -0.30831 | 56.8845
1170 | 19.5 | 2.0116 | 10.4371 | 2 | 10.4 | 39.3756 | 0 | -0.037102 | 128.216 | 0.00020109 | -0.11131 | 6.4108 | 0.00060326 | 6.3001 |  | 10.3001 | 4 | 10.3001 | 39.3756 | 19.6878 | 20 | 20 | -0.31219 | 56.5723
1171 | 19.5167 | 2.0115 | 10.4369 | 2 | 10.4 | 39.3679 | 0 | -0.036898 | 128.1791 | 0.00020362 | -0.11069 | 6.409 | 0.00061087 | 6.2989 |  | 10.2989 | 4 | 10.2989 | 39.3679 | 19.684 | 20 | 20 | -0.31603 | 56.2563
1172 | 19.5333 | 2.0115 | 10.4367 | 2 | 10.4 | 39.3604 | 0 | -0.036692 | 128.1424 | 0.00020612 | -0.11008 | 6.4071 | 0.00061837 | 6.2977 |  | 10.2977 | 4 | 10.2977 | 39.3604 | 19.6802 | 20 | 20 | -0.3198 | 55.9365
1173 | 19.55 | 2.0114 | 10.4365 | 2 | 10.4 | 39.3529 | 0 | -0.036483 | 128.1059 | 0.00020859 | -0.10945 | 6.4053 | 0.00062576 | 6.2965 |  | 10.2965 | 4 | 10.2965 | 39.3529 | 19.6765 | 20 | 20 | -0.32353 | 55.6129
1174 | 19.5667 | 2.0113 | 10.4363 | 2 | 10.4 | 39.3456 | 0 | -0.036272 | 128.0697 | 0.00021101 | -0.10882 | 6.4035 | 0.00063304 | 6.2953 |  | 10.2953 | 4 | 10.2953 | 39.3456 | 19.6728 | 20 | 20 | -0.32719 | 55.2857
1175 | 19.5833 | 2.0113 | 10.4361 | 2 | 10.4 | 39.3384 | 0 | -0.036059 | 128.0336 | 0.0002134 | -0.10818 | 6.4017 | 0.00064021 | 6.2941 |  | 10.2941 | 4 | 10.2941 | 39.3384 | 19.6692 | 20 | 20 | -0.3308 | 54.9549
1176 | 19.6 | 2.0112 | 10.4358 | 2 | 10.4 | 39.3313 | 0 | -0.035843 | 127.9977 | 0.00021576 | -0.10753 | 6.3999 | 0.00064728 | 6.293 |  | 10.293 | 4 | 10.293 | 39.3313 | 19.6656 | 20 | 20 | -0.33436 | 54.6206
1177 | 19.6167 | 2.0111 | 10.4356 | 2 | 10.4 | 39.3243 | 0 | -0.035625 | 127.9621 | 0.00021808 | -0.10688 | 6.3981 | 0.00065424 | 6.2919 |  | 10.2919 | 4 | 10.2919 | 39.3243 | 19.6621 | 20 | 20 | -0.33786 | 54.2827
1178 | 19.6333 | 2.0111 | 10.4354 | 2 | 10.4 | 39.3174 | 0 | -0.035405 | 127.9267 | 0.00022036 | -0.10621 | 6.3963 | 0.00066109 | 6.2908 |  | 10.2908 | 4 | 10.2908 | 39.3174 | 19.6587 | 20 | 20 | -0.3413 | 53.9414
1179 | 19.65 | 2.011 | 10.4352 | 2 | 10.4 | 39.3106 | 0 | -0.035182 | 127.8915 | 0.00022261 | -0.10555 | 6.3946 | 0.00066783 | 6.2897 |  | 10.2897 | 4 | 10.2897 | 39.3106 | 19.6553 | 20 | 20 | -0.34469 | 53.5967
1180 | 19.6667 | 2.0109 | 10.435 | 2 | 10.4 | 39.3039 | 0 | -0.034957 | 127.8566 | 0.00022482 | -0.10487 | 6.3928 | 0.00067446 | 6.2886 |  | 10.2886 | 4 | 10.2886 | 39.3039 | 19.652 | 20 | 20 | -0.34803 | 53.2487
1181 | 19.6833 | 2.0109 | 10.4347 | 2 | 10.4 | 39.2974 | 0 | -0.03473 | 127.8218 | 0.00022699 | -0.10419 | 6.3911 | 0.00068098 | 6.2876 |  | 10.2876 | 4 | 10.2876 | 39.2974 | 19.6487 | 20 | 20 | -0.35131 | 52.8974
1182 | 19.7 | 2.0108 | 10.4345 | 2 | 10.4 | 39.2909 | 0 | -0.034501 | 127.7873 | 0.00022913 | -0.1035 | 6.3894 | 0.00068739 | 6.2866 |  | 10.2866 | 4 | 10.2866 | 39.2909 | 19.6455 | 20 | 20 | -0.35453 | 52.5429
1183 | 19.7167 | 2.0107 | 10.4343 | 2 | 10.4 | 39.2846 | 0 | -0.03427 | 127.7531 | 0.00023123 | -0.10281 | 6.3877 | 0.0006937 | 6.2855 |  | 10.2855 | 4 | 10.2855 | 39.2846 | 19.6423 | 20 | 20 | -0.3577 | 52.1852
1184 | 19.7333 | 2.0106 | 10.434 | 2 | 10.4 | 39.2784 | 0 | -0.034037 | 127.719 | 0.0002333 | -0.10211 | 6.386 | 0.0006999 | 6.2845 |  | 10.2845 | 4 | 10.2845 | 39.2784 | 19.6392 | 20 | 20 | -0.36081 | 51.8244
1185 | 19.75 | 2.0106 | 10.4338 | 2 | 10.4 | 39.2723 | 0 | -0.033801 | 127.6852 | 0.00023533 | -0.1014 | 6.3843 | 0.00070599 | 6.2836 |  | 10.2836 | 4 | 10.2836 | 39.2723 | 19.6361 | 20 | 20 | -0.36386 | 51.4605
1186 | 19.7667 | 2.0105 | 10.4336 | 2 | 10.4 | 39.2663 | 0 | -0.033564 | 127.6517 | 0.00023732 | -0.10069 | 6.3826 | 0.00071197 | 6.2826 |  | 10.2826 | 4 | 10.2826 | 39.2663 | 19.6331 | 20 | 20 | -0.36686 | 51.0936
1187 | 19.7833 | 2.0104 | 10.4333 | 2 | 10.4 | 39.2604 | 0 | -0.033325 | 127.6183 | 0.00023928 | -0.099974 | 6.3809 | 0.00071784 | 6.2817 |  | 10.2817 | 4 | 10.2817 | 39.2604 | 19.6302 | 20 | 20 | -0.36981 | 50.7238
1188 | 19.8 | 2.0103 | 10.4331 | 2 | 10.4 | 39.2546 | 0 | -0.033084 | 127.5853 | 0.0002412 | -0.099251 | 6.3793 | 0.0007236 | 6.2807 |  | 10.2807 | 4 | 10.2807 | 39.2546 | 19.6273 | 20 | 20 | -0.3727 | 50.3511
1189 | 19.8167 | 2.0103 | 10.4328 | 2 | 10.4 | 39.2489 | 0 | -0.03284 | 127.5524 | 0.00024309 | -0.098521 | 6.3776 | 0.00072926 | 6.2798 |  | 10.2798 | 4 | 10.2798 | 39.2489 | 19.6245 | 20 | 20 | -0.37553 | 49.9756
1190 | 19.8333 | 2.0102 | 10.4326 | 2 | 10.4 | 39.2434 | 0 | -0.032596 | 127.5198 | 0.00024493 | -0.097787 | 6.376 | 0.0007348 | 6.2789 |  | 10.2789 | 4 | 10.2789 | 39.2434 | 19.6217 | 20 | 20 | -0.37831 | 49.5973
1191 | 19.85 | 2.0101 | 10.4323 | 2 | 10.4 | 39.2379 | 0 | -0.032349 | 127.4875 | 0.00024675 | -0.097046 | 6.3744 | 0.00074024 | 6.2781 |  | 10.2781 | 4 | 10.2781 | 39.2379 | 19.619 | 20 | 20 | -0.38104 | 49.2162
1192 | 19.8667 | 2.01 | 10.4321 | 2 | 10.4 | 39.2326 | 0 | -0.0321 | 127.4554 | 0.00024852 | -0.096301 | 6.3728 | 0.00074557 | 6.2772 |  | 10.2772 | 4 | 10.2772 | 39.2326 | 19.6163 | 20 | 20 | -0.38371 | 48.8325
1193 | 19.8833 | 2.01 | 10.4319 | 2 | 10.4 | 39.2274 | 0 | -0.03185 | 127.4235 | 0.00025026 | -0.09555 | 6.3712 | 0.00075079 | 6.2764 |  | 10.2764 | 4 | 10.2764 | 39.2274 | 19.6137 | 20 | 20 | -0.38632 | 48.4462
1194 | 19.9 | 2.0099 | 10.4316 | 2 | 10.4 | 39.2222 | 0 | -0.031598 | 127.3919 | 0.00025197 | -0.094794 | 6.3696 | 0.00075591 | 6.2756 |  | 10.2756 | 4 | 10.2756 | 39.2222 | 19.6111 | 20 | 20 | -0.38888 | 48.0573
1195 | 19.9167 | 2.0098 | 10.4313 | 2 | 10.4 | 39.2172 | 0 | -0.031344 | 127.3606 | 0.00025364 | -0.094033 | 6.368 | 0.00076092 | 6.2748 |  | 10.2748 | 4 | 10.2748 | 39.2172 | 19.6086 | 20 | 20 | -0.39138 | 47.6659
1196 | 19.9333 | 2.0097 | 10.4311 | 2 | 10.4 | 39.2123 | 0 | -0.031089 | 127.3295 | 0.00025527 | -0.093267 | 6.3665 | 0.00076582 | 6.274 |  | 10.274 | 4 | 10.274 | 39.2123 | 19.6062 | 20 | 20 | -0.39383 | 47.2721
1197 | 19.95 | 2.0096 | 10.4308 | 2 | 10.4 | 39.2075 | 0 | -0.030832 | 127.2987 | 0.00025687 | -0.092497 | 6.3649 | 0.00077061 | 6.2732 |  | 10.2732 | 4 | 10.2732 | 39.2075 | 19.6038 | 20 | 20 | -0.39623 | 46.8759
1198 | 19.9667 | 2.0096 | 10.4306 | 2 | 10.4 | 39.2029 | 0 | -0.030574 | 127.2681 | 0.00025843 | -0.091721 | 6.3634 | 0.00077529 | 6.2725 |  | 10.2725 | 4 | 10.2725 | 39.2029 | 19.6014 | 20 | 20 | -0.39857 | 46.4773
1199 | 19.9833 | 2.0095 | 10.4303 | 2 | 10.4 | 39.1983 | 0 | -0.030314 | 127.2378 | 0.00025996 | -0.090942 | 6.3619 | 0.00077987 | 6.2717 |  | 10.2717 | 4 | 10.2717 | 39.1983 | 19.5991 | 20 | 20 | -0.40085 | 46.0765
1200 | 20 | 2.0094 | 10.4301 | 2 | 10.4 | 39.1938 | 0 | -0.030052 | 127.2077 | 0.00026145 | -0.090157 | 6.3604 | 0.00078434 | 6.271 |  | 10.271 | 4 | 10.271 | 39.1938 | 19.5969 | 20 | 20 | -0.40308 | 45.6734
1201 | 20.0167 | 2.0093 | 10.4298 | 2 | 10.4 | 39.1895 | 0 | -0.02979 | 127.1779 | 0.0002629 | -0.089369 | 6.3589 | 0.00078871 | 6.2703 |  | 10.2703 | 4 | 10.2703 | 39.1895 | 19.5947 | 20 | 20 | -0.40526 | 45.2681
1202 | 20.0333 | 2.0092 | 10.4295 | 2 | 10.4 | 39.1852 | 0 | -0.029525 | 127.1484 | 0.00026432 | -0.088576 | 6.3574 | 0.00079297 | 6.2696 |  | 10.2696 | 4 | 10.2696 | 39.1852 | 19.5926 | 20 | 20 | -0.40738 | 44.8607
1203 | 20.05 | 2.0091 | 10.4293 | 2 | 10.4 | 39.1811 | 0 | -0.029259 | 127.1192 | 0.00026571 | -0.087778 | 6.356 | 0.00079712 | 6.269 |  | 10.269 | 4 | 10.269 | 39.1811 | 19.5906 | 20 | 20 | -0.40945 | 44.4513
1204 | 20.0667 | 2.0091 | 10.429 | 2 | 10.4 | 39.1771 | 0 | -0.028992 | 127.0902 | 0.00026705 | -0.086977 | 6.3545 | 0.00080116 | 6.2683 |  | 10.2683 | 4 | 10.2683 | 39.1771 | 19.5885 | 20 | 20 | -0.41146 | 44.0398
1205 | 20.0833 | 2.009 | 10.4287 | 2 | 10.4 | 39.1732 | 0 | -0.028724 | 127.0614 | 0.00026837 | -0.086172 | 6.3531 | 0.0008051 | 6.2677 |  | 10.2677 | 4 | 10.2677 | 39.1732 | 19.5866 | 20 | 20 | -0.41342 | 43.6264
1206 | 20.1 | 2.0089 | 10.4285 | 2 | 10.4 | 39.1693 | 0 | -0.028454 | 127.033 | 0.00026965 | -0.085363 | 6.3516 | 0.00080894 | 6.2671 |  | 10.2671 | 4 | 10.2671 | 39.1693 | 19.5847 | 20 | 20 | -0.41533 | 43.2111
1207 | 20.1167 | 2.0088 | 10.4282 | 2 | 10.4 | 39.1656 | 0 | -0.028184 | 127.0048 | 0.00027089 | -0.084551 | 6.3502 | 0.00081267 | 6.2665 |  | 10.2665 | 4 | 10.2665 | 39.1656 | 19.5828 | 20 | 20 | -0.41718 | 42.7939
1208 | 20.1333 | 2.0087 | 10.4279 | 2 | 10.4 | 39.162 | 0 | -0.027911 | 126.9769 | 0.0002721 | -0.083734 | 6.3488 | 0.00081629 | 6.2659 |  | 10.2659 | 4 | 10.2659 | 39.162 | 19.581 | 20 | 20 | -0.41898 | 42.3749
1209 | 20.15 | 2.0086 | 10.4276 | 2 | 10.4 | 39.1585 | 0 | -0.027638 | 126.9492 | 0.00027327 | -0.082914 | 6.3475 | 0.00081981 | 6.2654 |  | 10.2654 | 4 | 10.2654 | 39.1585 | 19.5793 | 20 | 20 | -0.42073 | 41.9542
1210 | 20.1667 | 2.0086 | 10.4274 | 2 | 10.4 | 39.1552 | 0 | -0.027364 | 126.9219 | 0.00027441 | -0.082091 | 6.3461 | 0.00082323 | 6.2648 |  | 10.2648 | 4 | 10.2648 | 39.1552 | 19.5776 | 20 | 20 | -0.42242 | 41.5318
1211 | 20.1833 | 2.0085 | 10.4271 | 2 | 10.4 | 39.1519 | 0 | -0.027088 | 126.8948 | 0.00027551 | -0.081265 | 6.3447 | 0.00082654 | 6.2643 |  | 10.2643 | 4 | 10.2643 | 39.1519 | 19.5759 | 20 | 20 | -0.42406 | 41.1077
1212 | 20.2 | 2.0084 | 10.4268 | 2 | 10.4 | 39.1487 | 0 | -0.026812 | 126.868 | 0.00027658 | -0.080435 | 6.3434 | 0.00082975 | 6.2638 |  | 10.2638 | 4 | 10.2638 | 39.1487 | 19.5744 | 20 | 20 | -0.42564 | 40.6821
1213 | 20.2167 | 2.0083 | 10.4265 | 2 | 10.4 | 39.1456 | 0 | -0.026534 | 126.8415 | 0.00027762 | -0.079602 | 6.3421 | 0.00083285 | 6.2633 |  | 10.2633 | 4 | 10.2633 | 39.1456 | 19.5728 | 20 | 20 | -0.42718 | 40.2549
1214 | 20.2333 | 2.0082 | 10.4263 | 2 | 10.4 | 39.1427 | 0 | -0.026255 | 126.8152 | 0.00027862 | -0.078766 | 6.3408 | 0.00083585 | 6.2628 |  | 10.2628 | 4 | 10.2628 | 39.1427 | 19.5713 | 20 | 20 | -0.42866 | 39.8262
1215 | 20.25 | 2.0081 | 10.426 | 2 | 10.4 | 39.1398 | 0 | -0.025976 | 126.7892 | 0.00027958 | -0.077928 | 6.3395 | 0.00083875 | 6.2624 |  | 10.2624 | 4 | 10.2624 | 39.1398 | 19.5699 | 20 | 20 | -0.43009 | 39.3962
1216 | 20.2667 | 2.008 | 10.4257 | 2 | 10.4 | 39.1371 | 0 | -0.025695 | 126.7635 | 0.00028052 | -0.077086 | 6.3382 | 0.00084155 | 6.2619 |  | 10.2619 | 4 | 10.2619 | 39.1371 | 19.5685 | 20 | 20 | -0.43146 | 38.9647
1217 | 20.2833 | 2.0079 | 10.4254 | 2 | 10.4 | 39.1344 | 0 | -0.025414 | 126.7381 | 0.00028141 | -0.076242 | 6.3369 | 0.00084424 | 6.2615 |  | 10.2615 | 4 | 10.2615 | 39.1344 | 19.5672 | 20 | 20 | -0.43279 | 38.5319
1218 | 20.3 | 2.0079 | 10.4251 | 2 | 10.4 | 39.1319 | 0 | -0.025132 | 126.713 | 0.00028228 | -0.075395 | 6.3356 | 0.00084683 | 6.2611 |  | 10.2611 | 4 | 10.2611 | 39.1319 | 19.5659 | 20 | 20 | -0.43406 | 38.0978
1219 | 20.3167 | 2.0078 | 10.4248 | 2 | 10.4 | 39.1294 | 0 | -0.024849 | 126.6881 | 0.00028311 | -0.074546 | 6.3344 | 0.00084932 | 6.2607 |  | 10.2607 | 4 | 10.2607 | 39.1294 | 19.5647 | 20 | 20 | -0.43528 | 37.6626
1220 | 20.3333 | 2.0077 | 10.4246 | 2 | 10.4 | 39.1271 | 0 | -0.024565 | 126.6636 | 0.0002839 | -0.073694 | 6.3332 | 0.00085171 | 6.2603 |  | 10.2603 | 4 | 10.2603 | 39.1271 | 19.5636 | 20 | 20 | -0.43645 | 37.2261
1221 | 20.35 | 2.0076 | 10.4243 | 2 | 10.4 | 39.1249 | 0 | -0.02428 | 126.6393 | 0.00028467 | -0.07284 | 6.332 | 0.000854 | 6.26 |  | 10.26 | 4 | 10.26 | 39.1249 | 19.5624 | 20 | 20 | -0.43757 | 36.7885
1222 | 20.3667 | 2.0075 | 10.424 | 2 | 10.4 | 39.1227 | 0 | -0.023995 | 126.6153 | 0.00028539 | -0.071984 | 6.3308 | 0.00085618 | 6.2596 |  | 10.2596 | 4 | 10.2596 | 39.1227 | 19.5614 | 20 | 20 | -0.43863 | 36.3499
1223 | 20.3833 | 2.0074 | 10.4237 | 2 | 10.4 | 39.1207 | 0 | -0.023708 | 126.5916 | 0.00028609 | -0.071125 | 6.3296 | 0.00085827 | 6.2593 |  | 10.2593 | 4 | 10.2593 | 39.1207 | 19.5603 | 20 | 20 | -0.43965 | 35.9103
1224 | 20.4 | 2.0073 | 10.4234 | 2 | 10.4 | 39.1188 | 0 | -0.023422 | 126.5682 | 0.00028675 | -0.070265 | 6.3284 | 0.00086026 | 6.259 |  | 10.259 | 4 | 10.259 | 39.1188 | 19.5594 | 20 | 20 | -0.44062 | 35.4696
1225 | 20.4167 | 2.0072 | 10.4231 | 2 | 10.4 | 39.1169 | 0 | -0.023134 | 126.545 | 0.00028738 | -0.069403 | 6.3273 | 0.00086215 | 6.2587 |  | 10.2587 | 4 | 10.2587 | 39.1169 | 19.5585 | 20 | 20 | -0.44153 | 35.0281
1226 | 20.4333 | 2.0071 | 10.4228 | 2 | 10.4 | 39.1152 | 0 | -0.022846 | 126.5222 | 0.00028798 | -0.068539 | 6.3261 | 0.00086394 | 6.2584 |  | 10.2584 | 4 | 10.2584 | 39.1152 | 19.5576 | 20 | 20 | -0.44239 | 34.5857
1227 | 20.45 | 2.007 | 10.4226 | 2 | 10.4 | 39.1136 | 0 | -0.022558 | 126.4996 | 0.00028854 | -0.067673 | 6.325 | 0.00086563 | 6.2582 |  | 10.2582 | 4 | 10.2582 | 39.1136 | 19.5568 | 20 | 20 | -0.44321 | 34.1425
1228 | 20.4667 | 2.007 | 10.4223 | 2 | 10.4 | 39.1121 | 0 | -0.022269 | 126.4774 | 0.00028907 | -0.066806 | 6.3239 | 0.00086722 | 6.2579 |  | 10.2579 | 4 | 10.2579 | 39.1121 | 19.556 | 20 | 20 | -0.44397 | 33.6985
1229 | 20.4833 | 2.0069 | 10.422 | 2 | 10.4 | 39.1106 | 0 | -0.021979 | 126.4554 | 0.00028957 | -0.065938 | 6.3228 | 0.00086872 | 6.2577 |  | 10.2577 | 4 | 10.2577 | 39.1106 | 19.5553 | 20 | 20 | -0.44469 | 33.2539
1230 | 20.5 | 2.0068 | 10.4217 | 2 | 10.4 | 39.1093 | 0 | -0.021689 | 126.4337 | 0.00029004 | -0.065067 | 6.3217 | 0.00087012 | 6.2575 |  | 10.2575 | 4 | 10.2575 | 39.1093 | 19.5546 | 20 | 20 | -0.44535 | 32.8085
1231 | 20.5167 | 2.0067 | 10.4214 | 2 | 10.4 | 39.1081 | 0 | -0.021399 | 126.4123 | 0.00029047 | -0.064196 | 6.3206 | 0.00087142 | 6.2573 |  | 10.2573 | 4 | 10.2573 | 39.1081 | 19.554 | 20 | 20 | -0.44597 | 32.3625
1232 | 20.5333 | 2.0066 | 10.4211 | 2 | 10.4 | 39.1069 | 0 | -0.021108 | 126.3912 | 0.00029087 | -0.063323 | 6.3196 | 0.00087262 | 6.2571 |  | 10.2571 | 4 | 10.2571 | 39.1069 | 19.5535 | 20 | 20 | -0.44654 | 31.916
1233 | 20.55 | 2.0065 | 10.4208 | 2 | 10.4 | 39.1059 | 0 | -0.020817 | 126.3704 | 0.00029124 | -0.06245 | 6.3185 | 0.00087373 | 6.2569 |  | 10.2569 | 4 | 10.2569 | 39.1059 | 19.5529 | 20 | 20 | -0.44706 | 31.4689
1234 | 20.5667 | 2.0064 | 10.4205 | 2 | 10.4 | 39.1049 | 0 | -0.020525 | 126.3498 | 0.00029158 | -0.061575 | 6.3175 | 0.00087475 | 6.2568 |  | 10.2568 | 4 | 10.2568 | 39.1049 | 19.5525 | 20 | 20 | -0.44753 | 31.0214
1235 | 20.5833 | 2.0063 | 10.4202 | 2 | 10.4 | 39.1041 | 0 | -0.020233 | 126.3296 | 0.00029189 | -0.060699 | 6.3165 | 0.00087567 | 6.2567 |  | 10.2567 | 4 | 10.2567 | 39.1041 | 19.5521 | 20 | 20 | -0.44795 | 30.5735
1236 | 20.6 | 2.0062 | 10.4199 | 2 | 10.4 | 39.1034 | 0 | -0.019941 | 126.3097 | 0.00029216 | -0.059823 | 6.3155 | 0.00087649 | 6.2565 |  | 10.2565 | 4 | 10.2565 | 39.1034 | 19.5517 | 20 | 20 | -0.44832 | 30.1251
1237 | 20.6167 | 2.0061 | 10.4196 | 2 | 10.4 | 39.1027 | 0 | -0.019649 | 126.29 | 0.00029241 | -0.058946 | 6.3145 | 0.00087723 | 6.2564 |  | 10.2564 | 4 | 10.2564 | 39.1027 | 19.5514 | 20 | 20 | -0.44865 | 29.6765
1238 | 20.6333 | 2.006 | 10.4194 | 2 | 10.4 | 39.1021 | 0 | -0.019356 | 126.2707 | 0.00029262 | -0.058068 | 6.3135 | 0.00087787 | 6.2563 |  | 10.2563 | 4 | 10.2563 | 39.1021 | 19.5511 | 20 | 20 | -0.44893 | 29.2276
1239 | 20.65 | 2.006 | 10.4191 | 2 | 10.4 | 39.1017 | 0 | -0.019063 | 126.2516 | 0.0002928 | -0.057189 | 6.3126 | 0.00087841 | 6.2563 |  | 10.2563 | 4 | 10.2563 | 39.1017 | 19.5508 | 20 | 20 | -0.44916 | 28.7784
1240 | 20.6667 | 2.0059 | 10.4188 | 2 | 10.4 | 39.1013 | 0 | -0.01877 | 126.2328 | 0.00029295 | -0.05631 | 6.3116 | 0.00087886 | 6.2562 |  | 10.2562 | 4 | 10.2562 | 39.1013 | 19.5507 | 20 | 20 | -0.44934 | 28.3291
1241 | 20.6833 | 2.0058 | 10.4185 | 2 | 10.4 | 39.101 | 0 | -0.018477 | 126.2143 | 0.00029308 | -0.055431 | 6.3107 | 0.00087923 | 6.2562 |  | 10.2562 | 4 | 10.2562 | 39.101 | 19.5505 | 20 | 20 | -0.44948 | 27.8796
1242 | 20.7 | 2.0057 | 10.4182 | 2 | 10.4 | 39.1009 | 0 | -0.018184 | 126.1962 | 0.00029317 | -0.054552 | 6.3098 | 0.0008795 | 6.2561 |  | 10.2561 | 4 | 10.2561 | 39.1009 | 19.5504 | 20 | 20 | -0.44957 | 27.43
1243 | 20.7167 | 2.0056 | 10.4179 | 2 | 10.4 | 39.1008 | 0 | -0.017891 | 126.1783 | 0.00029323 | -0.053672 | 6.3089 | 0.00087968 | 6.2561 |  | 10.2561 | 4 | 10.2561 | 39.1008 | 19.5504 | 20 | 20 | -0.44962 | 26.9804
1244 | 20.7333 | 2.0055 | 10.4176 | 2 | 10.4 | 39.1008 | 0 | -0.017597 | 126.1607 | 0.00029326 | -0.052792 | 6.308 | 0.00087977 | 6.2561 |  | 10.2561 | 4 | 10.2561 | 39.1008 | 19.5504 | 20 | 20 | -0.44962 | 26.5308
1245 | 20.75 | 2.0054 | 10.4173 | 2 | 10.4 | 39.1008 | 0 | -0.017304 | 126.1434 | 0.00029326 | -0.051912 | 6.3072 | 0.00087977 | 6.2561 |  | 10.2561 | 4 | 10.2561 | 39.1008 | 19.5504 | 20 | 20 | -0.44958 | 26.0812
1246 | 20.7667 | 2.0053 | 10.417 | 2 | 10.4 | 39.101 | 0 | -0.017011 | 126.1264 | 0.00029323 | -0.051033 | 6.3063 | 0.00087968 | 6.2562 |  | 10.2562 | 4 | 10.2562 | 39.101 | 19.5505 | 20 | 20 | -0.44948 | 25.6317
1247 | 20.7833 | 2.0052 | 10.4167 | 2 | 10.4 | 39.1013 | 0 | -0.016718 | 126.1096 | 0.00029317 | -0.050153 | 6.3055 | 0.0008795 | 6.2562 |  | 10.2562 | 4 | 10.2562 | 39.1013 | 19.5507 | 20 | 20 | -0.44935 | 25.1824
1248 | 20.8 | 2.0051 | 10.4164 | 2 | 10.4 | 39.1017 | 0 | -0.016425 | 126.0932 | 0.00029308 | -0.049274 | 6.3047 | 0.00087923 | 6.2563 |  | 10.2563 | 4 | 10.2563 | 39.1017 | 19.5508 | 20 | 20 | -0.44917 | 24.7332
1249 | 20.8167 | 2.005 | 10.4161 | 2 | 10.4 | 39.1021 | 0 | -0.016132 | 126.0771 | 0.00029296 | -0.048395 | 6.3039 | 0.00087888 | 6.2563 |  | 10.2563 | 4 | 10.2563 | 39.1021 | 19.5511 | 20 | 20 | -0.44894 | 24.2842
1250 | 20.8333 | 2.0049 | 10.4158 | 2 | 10.4 | 39.1027 | 0 | -0.015839 | 126.0612 | 0.00029281 | -0.047517 | 6.3031 | 0.00087844 | 6.2564 |  | 10.2564 | 4 | 10.2564 | 39.1027 | 19.5513 | 20 | 20 | -0.44867 | 23.8356
1251 | 20.85 | 2.0049 | 10.4155 | 2 | 10.4 | 39.1033 | 0 | -0.015546 | 126.0457 | 0.00029264 | -0.046639 | 6.3023 | 0.00087792 | 6.2565 |  | 10.2565 | 4 | 10.2565 | 39.1033 | 19.5516 | 20 | 20 | -0.44836 | 23.3872
1252 | 20.8667 | 2.0048 | 10.4153 | 2 | 10.4 | 39.104 | 0 | -0.015254 | 126.0304 | 0.00029243 | -0.045761 | 6.3015 | 0.0008773 | 6.2566 |  | 10.2566 | 4 | 10.2566 | 39.104 | 19.552 | 20 | 20 | -0.44801 | 22.9392
1253 | 20.8833 | 2.0047 | 10.415 | 2 | 10.4 | 39.1048 | 0 | -0.014962 | 126.0155 | 0.0002922 | -0.044885 | 6.3008 | 0.00087661 | 6.2568 |  | 10.2568 | 4 | 10.2568 | 39.1048 | 19.5524 | 20 | 20 | -0.44761 | 22.4916
1254 | 20.9 | 2.0046 | 10.4147 | 2 | 10.4 | 39.1057 | 0 | -0.01467 | 126.0008 | 0.00029194 | -0.044009 | 6.3 | 0.00087583 | 6.2569 |  | 10.2569 | 4 | 10.2569 | 39.1057 | 19.5528 | 20 | 20 | -0.44716 | 22.0444
1255 | 20.9167 | 2.0045 | 10.4144 | 2 | 10.4 | 39.1066 | 0 | -0.014378 | 125.9864 | 0.00029165 | -0.043134 | 6.2993 | 0.00087496 | 6.2571 |  | 10.2571 | 4 | 10.2571 | 39.1066 | 19.5533 | 20 | 20 | -0.44668 | 21.5978
1256 | 20.9333 | 2.0044 | 10.4141 | 2 | 10.4 | 39.1077 | 0 | -0.014087 | 125.9724 | 0.00029134 | -0.04226 | 6.2986 | 0.00087401 | 6.2572 |  | 10.2572 | 4 | 10.2572 | 39.1077 | 19.5538 | 20 | 20 | -0.44615 | 21.1516
1257 | 20.95 | 2.0043 | 10.4138 | 2 | 10.4 | 39.1088 | 0 | -0.013796 | 125.9586 | 0.00029099 | -0.041387 | 6.2979 | 0.00087298 | 6.2574 |  | 10.2574 | 4 | 10.2574 | 39.1088 | 19.5544 | 20 | 20 | -0.44558 | 20.706
1258 | 20.9667 | 2.0042 | 10.4135 | 2 | 10.4 | 39.1101 | 0 | -0.013505 | 125.9451 | 0.00029062 | -0.040515 | 6.2973 | 0.00087186 | 6.2576 |  | 10.2576 | 4 | 10.2576 | 39.1101 | 19.555 | 20 | 20 | -0.44497 | 20.2611
1259 | 20.9833 | 2.0041 | 10.4132 | 2 | 10.4 | 39.1114 | 0 | -0.013215 | 125.9318 | 0.00029022 | -0.039645 | 6.2966 | 0.00087067 | 6.2578 |  | 10.2578 | 4 | 10.2578 | 39.1114 | 19.5557 | 20 | 20 | -0.44432 | 19.8167
1260 | 21 | 2.004 | 10.4129 | 2 | 10.4 | 39.1127 | 0 | -0.012925 | 125.9189 | 0.0002898 | -0.038775 | 6.2959 | 0.00086939 | 6.258 |  | 10.258 | 4 | 10.258 | 39.1127 | 19.5564 | 20 | 20 | -0.44363 | 19.3731
1261 | 21.0167 | 2.0039 | 10.4126 | 2 | 10.4 | 39.1142 | 0 | -0.012636 | 125.9063 | 0.00028935 | -0.037907 | 6.2953 | 0.00086804 | 6.2583 |  | 10.2583 | 4 | 10.2583 | 39.1142 | 19.5571 | 20 | 20 | -0.44289 | 18.9302
1262 | 21.0333 | 2.0039 | 10.4123 | 2 | 10.4 | 39.1158 | 0 | -0.012347 | 125.8939 | 0.00028887 | -0.037041 | 6.2947 | 0.0008666 | 6.2585 |  | 10.2585 | 4 | 10.2585 | 39.1158 | 19.5579 | 20 | 20 | -0.44212 | 18.4881
1263 | 21.05 | 2.0038 | 10.4121 | 2 | 10.4 | 39.1174 | 0 | -0.012058 | 125.8819 | 0.00028836 | -0.036175 | 6.2941 | 0.00086508 | 6.2588 |  | 10.2588 | 4 | 10.2588 | 39.1174 | 19.5587 | 20 | 20 | -0.4413 | 18.0468
1264 | 21.0667 | 2.0037 | 10.4118 | 2 | 10.4 | 39.1191 | 0 | -0.011771 | 125.8701 | 0.00028783 | -0.035312 | 6.2935 | 0.00086349 | 6.2591 |  | 10.2591 | 4 | 10.2591 | 39.1191 | 19.5596 | 20 | 20 | -0.44045 | 17.6063
1265 | 21.0833 | 2.0036 | 10.4115 | 2 | 10.4 | 39.1209 | 0 | -0.011483 | 125.8586 | 0.00028727 | -0.03445 | 6.2929 | 0.00086182 | 6.2593 |  | 10.2593 | 4 | 10.2593 | 39.1209 | 19.5604 | 20 | 20 | -0.43955 | 17.1668
1266 | 21.1 | 2.0035 | 10.4112 | 2 | 10.4 | 39.1228 | 0 | -0.011197 | 125.8474 | 0.00028669 | -0.03359 | 6.2924 | 0.00086007 | 6.2596 |  | 10.2596 | 4 | 10.2596 | 39.1228 | 19.5614 | 20 | 20 | -0.43862 | 16.7282
1267 | 21.1167 | 2.0034 | 10.4109 | 2 | 10.4 | 39.1247 | 0 | -0.010911 | 125.8365 | 0.00028608 | -0.032732 | 6.2918 | 0.00085825 | 6.26 |  | 10.26 | 4 | 10.26 | 39.1247 | 19.5623 | 20 | 20 | -0.43765 | 16.2905
1268 | 21.1333 | 2.0033 | 10.4106 | 2 | 10.4 | 39.1267 | 0 | -0.010625 | 125.8259 | 0.00028545 | -0.031875 | 6.2913 | 0.00085634 | 6.2603 |  | 10.2603 | 4 | 10.2603 | 39.1267 | 19.5634 | 20 | 20 | -0.43664 | 15.8539
1269 | 21.15 | 2.0032 | 10.4103 | 2 | 10.4 | 39.1288 | 0 | -0.01034 | 125.8155 | 0.00028479 | -0.031021 | 6.2908 | 0.00085437 | 6.2606 |  | 10.2606 | 4 | 10.2606 | 39.1288 | 19.5644 | 20 | 20 | -0.43559 | 15.4183
1270 | 21.1667 | 2.0031 | 10.4101 | 2 | 10.4 | 39.131 | 0 | -0.010056 | 125.8055 | 0.00028411 | -0.030169 | 6.2903 | 0.00085232 | 6.261 |  | 10.261 | 4 | 10.261 | 39.131 | 19.5655 | 20 | 20 | -0.43451 | 14.9838
1271 | 21.1833 | 2.0031 | 10.4098 | 2 | 10.4 | 39.1332 | 0 | -0.0097729 | 125.7957 | 0.0002834 | -0.029319 | 6.2898 | 0.00085019 | 6.2613 |  | 10.2613 | 4 | 10.2613 | 39.1332 | 19.5666 | 20 | 20 | -0.43338 | 14.5504
1272 | 21.2 | 2.003 | 10.4095 | 2 | 10.4 | 39.1356 | 0 | -0.0094902 | 125.7862 | 0.00028267 | -0.028471 | 6.2893 | 0.000848 | 6.2617 |  | 10.2617 | 4 | 10.2617 | 39.1356 | 19.5678 | 20 | 20 | -0.43222 | 14.1182
1273 | 21.2167 | 2.0029 | 10.4092 | 2 | 10.4 | 39.1379 | 0 | -0.0092083 | 125.777 | 0.00028191 | -0.027625 | 6.2889 | 0.00084573 | 6.2621 |  | 10.2621 | 4 | 10.2621 | 39.1379 | 19.569 | 20 | 20 | -0.43103 | 13.6872
1274 | 21.2333 | 2.0028 | 10.4089 | 2 | 10.4 | 39.1404 | 0 | -0.0089272 | 125.7681 | 0.00028113 | -0.026781 | 6.2884 | 0.00084338 | 6.2625 |  | 10.2625 | 4 | 10.2625 | 39.1404 | 19.5702 | 20 | 20 | -0.42979 | 13.2574
1275 | 21.25 | 2.0027 | 10.4086 | 2 | 10.4 | 39.143 | 0 | -0.0086468 | 125.7594 | 0.00028032 | -0.025941 | 6.288 | 0.00084097 | 6.2629 |  | 10.2629 | 4 | 10.2629 | 39.143 | 19.5715 | 20 | 20 | -0.42852 | 12.8288
1276 | 21.2667 | 2.0026 | 10.4084 | 2 | 10.4 | 39.1456 | 0 | -0.0083673 | 125.7511 | 0.0002795 | -0.025102 | 6.2876 | 0.00083849 | 6.2633 |  | 10.2633 | 4 | 10.2633 | 39.1456 | 19.5728 | 20 | 20 | -0.42722 | 12.4016
1277 | 21.2833 | 2.0025 | 10.4081 | 2 | 10.4 | 39.1482 | 0 | -0.0080887 | 125.743 | 0.00027864 | -0.024266 | 6.2871 | 0.00083593 | 6.2637 |  | 10.2637 | 4 | 10.2637 | 39.1482 | 19.5741 | 20 | 20 | -0.42588 | 11.9757
1278 | 21.3 | 2.0024 | 10.4078 | 2 | 10.4 | 39.151 | 0 | -0.0078109 | 125.7352 | 0.00027777 | -0.023433 | 6.2868 | 0.00083331 | 6.2642 |  | 10.2642 | 4 | 10.2642 | 39.151 | 19.5755 | 20 | 20 | -0.4245 | 11.5512
1279 | 21.3167 | 2.0024 | 10.4075 | 2 | 10.4 | 39.1538 | 0 | -0.0075341 | 125.7276 | 0.00027687 | -0.022602 | 6.2864 | 0.00083062 | 6.2646 |  | 10.2646 | 4 | 10.2646 | 39.1538 | 19.5769 | 20 | 20 | -0.42309 | 11.1281
1280 | 21.3333 | 2.0023 | 10.4073 | 2 | 10.4 | 39.1567 | 0 | -0.0072581 | 125.7204 | 0.00027595 | -0.021774 | 6.286 | 0.00082786 | 6.2651 |  | 10.2651 | 4 | 10.2651 | 39.1567 | 19.5784 | 20 | 20 | -0.42165 | 10.7065
1281 | 21.35 | 2.0022 | 10.407 | 2 | 10.4 | 39.1597 | 0 | -0.0069831 | 125.7134 | 0.00027501 | -0.020949 | 6.2857 | 0.00082503 | 6.2655 |  | 10.2655 | 4 | 10.2655 | 39.1597 | 19.5798 | 20 | 20 | -0.42017 | 10.2863
1282 | 21.3667 | 2.0021 | 10.4067 | 2 | 10.4 | 39.1627 | 0 | -0.006709 | 125.7067 | 0.00027405 | -0.020127 | 6.2853 | 0.00082214 | 6.266 |  | 10.266 | 4 | 10.266 | 39.1627 | 19.5813 | 20 | 20 | -0.41866 | 9.8677
1283 | 21.3833 | 2.002 | 10.4064 | 2 | 10.4 | 39.1658 | 0 | -0.006436 | 125.7003 | 0.00027306 | -0.019308 | 6.285 | 0.00081918 | 6.2665 |  | 10.2665 | 4 | 10.2665 | 39.1658 | 19.5829 | 20 | 20 | -0.41711 | 9.4506
1284 | 21.4 | 2.0019 | 10.4062 | 2 | 10.4 | 39.1689 | 0 | -0.0061639 | 125.6941 | 0.00027205 | -0.018492 | 6.2847 | 0.00081616 | 6.267 |  | 10.267 | 4 | 10.267 | 39.1689 | 19.5845 | 20 | 20 | -0.41553 | 9.035
1285 | 21.4167 | 2.0018 | 10.4059 | 2 | 10.4 | 39.1722 | 0 | -0.0058929 | 125.6882 | 0.00027102 | -0.017679 | 6.2844 | 0.00081307 | 6.2675 |  | 10.2675 | 4 | 10.2675 | 39.1722 | 19.5861 | 20 | 20 | -0.41392 | 8.6211
1286 | 21.4333 | 2.0018 | 10.4056 | 2 | 10.4 | 39.1754 | 0 | -0.0056229 | 125.6826 | 0.00026997 | -0.016869 | 6.2841 | 0.00080992 | 6.2681 |  | 10.2681 | 4 | 10.2681 | 39.1754 | 19.5877 | 20 | 20 | -0.41228 | 8.2088
1287 | 21.45 | 2.0017 | 10.4054 | 2 | 10.4 | 39.1788 | 0 | -0.005354 | 125.6772 | 0.0002689 | -0.016062 | 6.2839 | 0.00080671 | 6.2686 |  | 10.2686 | 4 | 10.2686 | 39.1788 | 19.5894 | 20 | 20 | -0.41061 | 7.7982
1288 | 21.4667 | 2.0016 | 10.4051 | 2 | 10.4 | 39.1822 | 0 | -0.0050862 | 125.6721 | 0.00026781 | -0.015259 | 6.2836 | 0.00080343 | 6.2692 |  | 10.2692 | 4 | 10.2692 | 39.1822 | 19.5911 | 20 | 20 | -0.4089 | 7.3893
1289 | 21.4833 | 2.0015 | 10.4048 | 2 | 10.4 | 39.1857 | 0 | -0.0048195 | 125.6673 | 0.0002667 | -0.014459 | 6.2834 | 0.00080009 | 6.2697 |  | 10.2697 | 4 | 10.2697 | 39.1857 | 19.5928 | 20 | 20 | -0.40716 | 6.9821
1290 | 21.5 | 2.0014 | 10.4046 | 2 | 10.4 | 39.1892 | 0 | -0.004554 | 125.6628 | 0.00026556 | -0.013662 | 6.2831 | 0.00079669 | 6.2703 |  | 10.2703 | 4 | 10.2703 | 39.1892 | 19.5946 | 20 | 20 | -0.4054 | 6.5767
1291 | 21.5167 | 2.0013 | 10.4043 | 2 | 10.4 | 39.1928 | 0 | -0.0042895 | 125.6585 | 0.00026441 | -0.012869 | 6.2829 | 0.00079324 | 6.2708 |  | 10.2708 | 4 | 10.2708 | 39.1928 | 19.5964 | 20 | 20 | -0.4036 | 6.1731
1292 | 21.5333 | 2.0013 | 10.404 | 2 | 10.4 | 39.1965 | 0 | -0.0040263 | 125.6544 | 0.00026324 | -0.012079 | 6.2827 | 0.00078972 | 6.2714 |  | 10.2714 | 4 | 10.2714 | 39.1965 | 19.5982 | 20 | 20 | -0.40177 | 5.7714
1293 | 21.55 | 2.0012 | 10.4038 | 2 | 10.4 | 39.2002 | 0 | -0.0037643 | 125.6507 | 0.00026205 | -0.011293 | 6.2825 | 0.00078614 | 6.272 |  | 10.272 | 4 | 10.272 | 39.2002 | 19.6001 | 20 | 20 | -0.39991 | 5.3715
1294 | 21.5667 | 2.0011 | 10.4035 | 2 | 10.4 | 39.2039 | 0 | -0.0035034 | 125.6472 | 0.00026084 | -0.01051 | 6.2824 | 0.00078251 | 6.2726 |  | 10.2726 | 4 | 10.2726 | 39.2039 | 19.602 | 20 | 20 | -0.39803 | 4.9734
1295 | 21.5833 | 2.001 | 10.4032 | 2 | 10.4 | 39.2078 | 0 | -0.0032438 | 125.6439 | 0.00025961 | -0.0097315 | 6.2822 | 0.00077882 | 6.2732 |  | 10.2732 | 4 | 10.2732 | 39.2078 | 19.6039 | 20 | 20 | -0.39611 | 4.5773
1296 | 21.6 | 2.0009 | 10.403 | 2 | 10.4 | 39.2117 | 0 | -0.0029855 | 125.6409 | 0.00025836 | -0.0089564 | 6.282 | 0.00077507 | 6.2739 |  | 10.2739 | 4 | 10.2739 | 39.2117 | 19.6058 | 20 | 20 | -0.39417 | 4.1832
1297 | 21.6167 | 2.0009 | 10.4027 | 2 | 10.4 | 39.2156 | 0 | -0.0027284 | 125.6382 | 0.00025709 | -0.0081851 | 6.2819 | 0.00077126 | 6.2745 |  | 10.2745 | 4 | 10.2745 | 39.2156 | 19.6078 | 20 | 20 | -0.3922 | 3.791
1298 | 21.6333 | 2.0008 | 10.4025 | 2 | 10.4 | 39.2196 | 0 | -0.0024726 | 125.6357 | 0.0002558 | -0.0074177 | 6.2818 | 0.00076741 | 6.2751 |  | 10.2751 | 4 | 10.2751 | 39.2196 | 19.6098 | 20 | 20 | -0.3902 | 3.4008
1299 | 21.65 | 2.0007 | 10.4022 | 2 | 10.4 | 39.2237 | 0 | -0.0022181 | 125.6335 | 0.0002545 | -0.0066542 | 6.2817 | 0.00076349 | 6.2758 |  | 10.2758 | 4 | 10.2758 | 39.2237 | 19.6118 | 20 | 20 | -0.38817 | 3.0126
1300 | 21.6667 | 2.0006 | 10.402 | 2 | 10.4 | 39.2278 | 0 | -0.0019649 | 125.6316 | 0.00025318 | -0.0058947 | 6.2816 | 0.00075953 | 6.2764 |  | 10.2764 | 4 | 10.2764 | 39.2278 | 19.6139 | 20 | 20 | -0.38612 | 2.6265
1301 | 21.6833 | 2.0005 | 10.4017 | 2 | 10.4 | 39.2319 | 0 | -0.0017131 | 125.6299 | 0.00025184 | -0.0051392 | 6.2815 | 0.00075551 | 6.2771 |  | 10.2771 | 4 | 10.2771 | 39.2319 | 19.616 | 20 | 20 | -0.38403 | 2.2424
1302 | 21.7 | 2.0005 | 10.4015 | 2 | 10.4 | 39.2361 | 0 | -0.0014626 | 125.6284 | 0.00025048 | -0.0043878 | 6.2814 | 0.00075144 | 6.2778 |  | 10.2778 | 4 | 10.2778 | 39.2361 | 19.6181 | 20 | 20 | -0.38193 | 1.8605
1303 | 21.7167 | 2.0004 | 10.4012 | 2 | 10.4 | 39.2404 | 0 | -0.0012135 | 125.6272 | 0.0002491 | -0.0036404 | 6.2814 | 0.00074731 | 6.2785 |  | 10.2785 | 4 | 10.2785 | 39.2404 | 19.6202 | 20 | 20 | -0.37979 | 1.4807
1304 | 21.7333 | 2.0003 | 10.401 | 2 | 10.4 | 39.2447 | 0 | -0.00096577 | 125.6262 | 0.00024771 | -0.0028973 | 6.2813 | 0.00074314 | 6.2792 |  | 10.2792 | 4 | 10.2792 | 39.2447 | 19.6224 | 20 | 20 | -0.37764 | 1.1031
1305 | 21.75 | 2.0002 | 10.4007 | 2 | 10.4 | 39.2491 | 0 | -0.00071946 | 125.6255 | 0.00024631 | -0.0021584 | 6.2813 | 0.00073892 | 6.2799 |  | 10.2799 | 4 | 10.2799 | 39.2491 | 19.6245 | 20 | 20 | -0.37545 | 0.72763
1306 | 21.7667 | 2.0001 | 10.4005 | 2 | 10.4 | 39.2535 | 0 | -0.00047458 | 125.625 | 0.00024488 | -0.0014237 | 6.2813 | 0.00073464 | 6.2806 |  | 10.2806 | 4 | 10.2806 | 39.2535 | 19.6268 | 20 | 20 | -0.37324 | 0.35439
1307 | 21.7833 | 2.0001 | 10.4002 | 2 | 10.4 | 39.258 | 0 | -0.00023114 | 125.6248 | 0.00024344 | -0.00069342 | 6.2812 | 0.00073032 | 6.2813 |  | 10.2813 | 4 | 10.2813 | 39.258 | 19.629 | 20 | 20 | -0.37101 | -0.016626
1308 | 21.8 | 2 | 10.4 | 2 | 10.4 | 39.2625 | 0 | 1.0844e-05 | 125.6248 | 0.00024198 | 3.2531e-05 | 6.2812 | 0.00072595 | 6.282 |  | 10.282 | 4 | 10.282 | 39.2625 | 19.6312 | 20 | 20 | -0.36876 | -0.38538
1309 | 21.8167 | 1.9999 | 10.3997 | 2 | 10.4 | 39.267 | 0 | 0.00025136 | 125.625 | 0.00024051 | 0.00075407 | 6.2813 | 0.00072154 | 6.2827 |  | 10.2827 | 4 | 10.2827 | 39.267 | 19.6335 | 20 | 20 | -0.36648 | -0.75186
1310 | 21.8333 | 1.9998 | 10.3995 | 2 | 10.4 | 39.2717 | 0 | 0.00049038 | 125.6255 | 0.00023903 | 0.0014711 | 6.2813 | 0.00071708 | 6.2835 |  | 10.2835 | 4 | 10.2835 | 39.2717 | 19.6358 | 20 | 20 | -0.36417 | -1.116
1311 | 21.85 | 1.9998 | 10.3993 | 2 | 10.4 | 39.2763 | 0 | 0.00072791 | 125.6263 | 0.00023752 | 0.0021837 | 6.2813 | 0.00071257 | 6.2842 |  | 10.2842 | 4 | 10.2842 | 39.2763 | 19.6382 | 20 | 20 | -0.36185 | -1.4779
1312 | 21.8667 | 1.9997 | 10.399 | 2 | 10.4 | 39.281 | 0 | 0.00096391 | 125.6272 | 0.00023601 | 0.0028917 | 6.2814 | 0.00070802 | 6.285 |  | 10.285 | 4 | 10.285 | 39.281 | 19.6405 | 20 | 20 | -0.3595 | -1.8374
1313 | 21.8833 | 1.9996 | 10.3988 | 2 | 10.4 | 39.2857 | 0 | 0.0011984 | 125.6284 | 0.00023447 | 0.0035952 | 6.2814 | 0.00070342 | 6.2857 |  | 10.2857 | 4 | 10.2857 | 39.2857 | 19.6429 | 20 | 20 | -0.35713 | -2.1945
1314 | 21.9 | 1.9996 | 10.3986 | 2 | 10.4 | 39.2905 | 0 | 0.0014313 | 125.6299 | 0.00023293 | 0.0042939 | 6.2815 | 0.00069878 | 6.2865 |  | 10.2865 | 4 | 10.2865 | 39.2905 | 19.6453 | 20 | 20 | -0.35473 | -2.5492
1315 | 21.9167 | 1.9995 | 10.3983 | 2 | 10.4 | 39.2954 | 0 | 0.0016627 | 125.6315 | 0.00023137 | 0.004988 | 6.2816 | 0.0006941 | 6.2873 |  | 10.2873 | 4 | 10.2873 | 39.2954 | 19.6477 | 20 | 20 | -0.35232 | -2.9015
1316 | 21.9333 | 1.9994 | 10.3981 | 2 | 10.4 | 39.3002 | 0 | 0.0018925 | 125.6334 | 0.00022979 | 0.0056774 | 6.2817 | 0.00068938 | 6.288 |  | 10.288 | 4 | 10.288 | 39.3002 | 19.6501 | 20 | 20 | -0.34988 | -3.2514
1317 | 21.95 | 1.9993 | 10.3979 | 2 | 10.4 | 39.3051 | 0 | 0.0021207 | 125.6355 | 0.0002282 | 0.006362 | 6.2818 | 0.00068461 | 6.2888 |  | 10.2888 | 4 | 10.2888 | 39.3051 | 19.6526 | 20 | 20 | -0.34743 | -3.5989
1318 | 21.9667 | 1.9993 | 10.3977 | 2 | 10.4 | 39.3101 | 0 | 0.0023473 | 125.6379 | 0.0002266 | 0.0070418 | 6.2819 | 0.00067981 | 6.2896 |  | 10.2896 | 4 | 10.2896 | 39.3101 | 19.655 | 20 | 20 | -0.34495 | -3.9438
1319 | 21.9833 | 1.9992 | 10.3974 | 2 | 10.4 | 39.3151 | 0 | 0.0025723 | 125.6405 | 0.00022499 | 0.0077168 | 6.282 | 0.00067496 | 6.2904 |  | 10.2904 | 4 | 10.2904 | 39.3151 | 19.6575 | 20 | 20 | -0.34245 | -4.2863
1320 | 22 | 1.9991 | 10.3972 | 2 | 10.4 | 39.3201 | 0 | 0.0027956 | 125.6433 | 0.00022336 | 0.0083869 | 6.2822 | 0.00067008 | 6.2912 |  | 10.2912 | 4 | 10.2912 | 39.3201 | 19.6601 | 20 | 20 | -0.33994 | -4.6262
1321 | 22.0167 | 1.9991 | 10.397 | 2 | 10.4 | 39.3252 | 0 | 0.0030173 | 125.6463 | 0.00022172 | 0.009052 | 6.2823 | 0.00066515 | 6.292 |  | 10.292 | 4 | 10.292 | 39.3252 | 19.6626 | 20 | 20 | -0.3374 | -4.9636
1322 | 22.0333 | 1.999 | 10.3968 | 2 | 10.4 | 39.3303 | 0 | 0.0032374 | 125.6495 | 0.00022007 | 0.0097122 | 6.2825 | 0.0006602 | 6.2928 |  | 10.2928 | 4 | 10.2928 | 39.3303 | 19.6651 | 20 | 20 | -0.33485 | -5.2985
1323 | 22.05 | 1.9989 | 10.3965 | 2 | 10.4 | 39.3354 | 0 | 0.0034558 | 125.653 | 0.0002184 | 0.010367 | 6.2826 | 0.0006552 | 6.2937 |  | 10.2937 | 4 | 10.2937 | 39.3354 | 19.6677 | 20 | 20 | -0.33228 | -5.6307
1324 | 22.0667 | 1.9989 | 10.3963 | 2 | 10.4 | 39.3406 | 0 | 0.0036725 | 125.6566 | 0.00021672 | 0.011018 | 6.2828 | 0.00065017 | 6.2945 |  | 10.2945 | 4 | 10.2945 | 39.3406 | 19.6703 | 20 | 20 | -0.32969 | -5.9604
1325 | 22.0833 | 1.9988 | 10.3961 | 2 | 10.4 | 39.3458 | 0 | 0.0038876 | 125.6605 | 0.00021503 | 0.011663 | 6.283 | 0.0006451 | 6.2953 |  | 10.2953 | 4 | 10.2953 | 39.3458 | 19.6729 | 20 | 20 | -0.32708 | -6.2875
1326 | 22.1 | 1.9987 | 10.3959 | 2 | 10.4 | 39.3511 | 0 | 0.0041009 | 125.6646 | 0.00021333 | 0.012303 | 6.2832 | 0.00064 | 6.2962 |  | 10.2962 | 4 | 10.2962 | 39.3511 | 19.6755 | 20 | 20 | -0.32446 | -6.612
1327 | 22.1167 | 1.9987 | 10.3957 | 2 | 10.4 | 39.3564 | 0 | 0.0043125 | 125.6689 | 0.00021162 | 0.012938 | 6.2834 | 0.00063486 | 6.297 |  | 10.297 | 4 | 10.297 | 39.3564 | 19.6782 | 20 | 20 | -0.32182 | -6.9338
1328 | 22.1333 | 1.9986 | 10.3955 | 2 | 10.4 | 39.3617 | 0 | 0.0045224 | 125.6735 | 0.0002099 | 0.013567 | 6.2837 | 0.00062969 | 6.2979 |  | 10.2979 | 4 | 10.2979 | 39.3617 | 19.6808 | 20 | 20 | -0.31916 | -7.2529
1329 | 22.15 | 1.9985 | 10.3953 | 2 | 10.4 | 39.367 | 0 | 0.0047306 | 125.6782 | 0.00020816 | 0.014192 | 6.2839 | 0.00062449 | 6.2987 |  | 10.2987 | 4 | 10.2987 | 39.367 | 19.6835 | 20 | 20 | -0.31648 | -7.5694
1330 | 22.1667 | 1.9985 | 10.3951 | 2 | 10.4 | 39.3724 | 0 | 0.004937 | 125.6831 | 0.00020642 | 0.014811 | 6.2842 | 0.00061926 | 6.2996 |  | 10.2996 | 4 | 10.2996 | 39.3724 | 19.6862 | 20 | 20 | -0.31379 | -7.8832
1331 | 22.1833 | 1.9984 | 10.3949 | 2 | 10.4 | 39.3778 | 0 | 0.0051417 | 125.6883 | 0.00020466 | 0.015425 | 6.2844 | 0.00061399 | 6.3005 |  | 10.3005 | 4 | 10.3005 | 39.3778 | 19.6889 | 20 | 20 | -0.31109 | -8.1943
1332 | 22.2 | 1.9983 | 10.3947 | 2 | 10.4 | 39.3833 | 0 | 0.0053446 | 125.6936 | 0.0002029 | 0.016034 | 6.2847 | 0.0006087 | 6.3013 |  | 10.3013 | 4 | 10.3013 | 39.3833 | 19.6916 | 20 | 20 | -0.30837 | -8.5027
1333 | 22.2167 | 1.9983 | 10.3945 | 2 | 10.4 | 39.3887 | 0 | 0.0055457 | 125.6992 | 0.00020113 | 0.016637 | 6.285 | 0.00060338 | 6.3022 |  | 10.3022 | 4 | 10.3022 | 39.3887 | 19.6944 | 20 | 20 | -0.30563 | -8.8083
1334 | 22.2333 | 1.9982 | 10.3943 | 2 | 10.4 | 39.3942 | 0 | 0.005745 | 125.7049 | 0.00019934 | 0.017235 | 6.2852 | 0.00059802 | 6.3031 |  | 10.3031 | 4 | 10.3031 | 39.3942 | 19.6971 | 20 | 20 | -0.30288 | -9.1112
1335 | 22.25 | 1.9981 | 10.3941 | 2 | 10.4 | 39.3998 | 0 | 0.0059426 | 125.7108 | 0.00019755 | 0.017828 | 6.2855 | 0.00059264 | 6.304 |  | 10.304 | 4 | 10.304 | 39.3998 | 19.6999 | 20 | 20 | -0.30012 | -9.4113
1336 | 22.2667 | 1.9981 | 10.3939 | 2 | 10.4 | 39.4053 | 0 | 0.0061383 | 125.717 | 0.00019575 | 0.018415 | 6.2858 | 0.00058724 | 6.3049 |  | 10.3049 | 4 | 10.3049 | 39.4053 | 19.7027 | 20 | 20 | -0.29734 | -9.7086
1337 | 22.2833 | 1.998 | 10.3937 | 2 | 10.4 | 39.4109 | 0 | 0.0063323 | 125.7233 | 0.00019393 | 0.018997 | 6.2862 | 0.0005818 | 6.3057 |  | 10.3057 | 4 | 10.3057 | 39.4109 | 19.7055 | 20 | 20 | -0.29455 | -10.0032
1338 | 22.3 | 1.998 | 10.3935 | 2 | 10.4 | 39.4165 | 0 | 0.0065244 | 125.7298 | 0.00019211 | 0.019573 | 6.2865 | 0.00057634 | 6.3066 |  | 10.3066 | 4 | 10.3066 | 39.4165 | 19.7083 | 20 | 20 | -0.29175 | -10.2949
1339 | 22.3167 | 1.9979 | 10.3933 | 2 | 10.4 | 39.4221 | 0 | 0.0067147 | 125.7366 | 0.00019029 | 0.020144 | 6.2868 | 0.00057086 | 6.3075 |  | 10.3075 | 4 | 10.3075 | 39.4221 | 19.7111 | 20 | 20 | -0.28893 | -10.5839
1340 | 22.3333 | 1.9978 | 10.3931 | 2 | 10.4 | 39.4278 | 0 | 0.0069031 | 125.7435 | 0.00018845 | 0.020709 | 6.2872 | 0.00056535 | 6.3084 |  | 10.3084 | 4 | 10.3084 | 39.4278 | 19.7139 | 20 | 20 | -0.2861 | -10.87
1341 | 22.35 | 1.9978 | 10.3929 | 2 | 10.4 | 39.4335 | 0 | 0.0070897 | 125.7505 | 0.0001866 | 0.021269 | 6.2875 | 0.00055981 | 6.3094 |  | 10.3094 | 4 | 10.3094 | 39.4335 | 19.7167 | 20 | 20 | -0.28326 | -11.1532
1342 | 22.3667 | 1.9977 | 10.3927 | 2 | 10.4 | 39.4392 | 0 | 0.0072745 | 125.7578 | 0.00018475 | 0.021823 | 6.2879 | 0.00055425 | 6.3103 |  | 10.3103 | 4 | 10.3103 | 39.4392 | 19.7196 | 20 | 20 | -0.28041 | -11.4336
1343 | 22.3833 | 1.9977 | 10.3925 | 2 | 10.4 | 39.4449 | 0 | 0.0074573 | 125.7653 | 0.00018289 | 0.022372 | 6.2883 | 0.00054868 | 6.3112 |  | 10.3112 | 4 | 10.3112 | 39.4449 | 19.7225 | 20 | 20 | -0.27755 | -11.7112
1344 | 22.4 | 1.9976 | 10.3924 | 2 | 10.4 | 39.4507 | 0 | 0.0076384 | 125.7729 | 0.00018102 | 0.022915 | 6.2886 | 0.00054307 | 6.3121 |  | 10.3121 | 4 | 10.3121 | 39.4507 | 19.7253 | 20 | 20 | -0.27467 | -11.9858
1345 | 22.4167 | 1.9976 | 10.3922 | 2 | 10.4 | 39.4564 | 0 | 0.0078175 | 125.7807 | 0.00017915 | 0.023453 | 6.289 | 0.00053745 | 6.313 |  | 10.313 | 4 | 10.313 | 39.4564 | 19.7282 | 20 | 20 | -0.27179 | -12.2576
1346 | 22.4333 | 1.9975 | 10.392 | 2 | 10.4 | 39.4622 | 0 | 0.0079948 | 125.7887 | 0.00017727 | 0.023984 | 6.2894 | 0.00053181 | 6.314 |  | 10.314 | 4 | 10.314 | 39.4622 | 19.7311 | 20 | 20 | -0.2689 | -12.5265
1347 | 22.45 | 1.9974 | 10.3918 | 2 | 10.4 | 39.468 | 0 | 0.0081702 | 125.7969 | 0.00017538 | 0.024511 | 6.2898 | 0.00052615 | 6.3149 |  | 10.3149 | 4 | 10.3149 | 39.468 | 19.734 | 20 | 20 | -0.26599 | -12.7925
1348 | 22.4667 | 1.9974 | 10.3917 | 2 | 10.4 | 39.4738 | 0 | 0.0083437 | 125.8052 | 0.00017349 | 0.025031 | 6.2903 | 0.00052047 | 6.3158 |  | 10.3158 | 4 | 10.3158 | 39.4738 | 19.7369 | 20 | 20 | -0.26308 | -13.0556
1349 | 22.4833 | 1.9973 | 10.3915 | 2 | 10.4 | 39.4797 | 0 | 0.0085153 | 125.8138 | 0.00017159 | 0.025546 | 6.2907 | 0.00051477 | 6.3167 |  | 10.3167 | 4 | 10.3167 | 39.4797 | 19.7398 | 20 | 20 | -0.26016 | -13.3158
1350 | 22.5 | 1.9973 | 10.3913 | 2 | 10.4 | 39.4855 | 0 | 0.0086849 | 125.8224 | 0.00016968 | 0.026055 | 6.2911 | 0.00050905 | 6.3177 |  | 10.3177 | 4 | 10.3177 | 39.4855 | 19.7428 | 20 | 20 | -0.25723 | -13.573
1351 | 22.5167 | 1.9972 | 10.3911 | 2 | 10.4 | 39.4914 | 0 | 0.0088527 | 125.8313 | 0.00016777 | 0.026558 | 6.2916 | 0.00050332 | 6.3186 |  | 10.3186 | 4 | 10.3186 | 39.4914 | 19.7457 | 20 | 20 | -0.25429 | -13.8273
1352 | 22.5333 | 1.9972 | 10.391 | 2 | 10.4 | 39.4973 | 0 | 0.0090186 | 125.8403 | 0.00016586 | 0.027056 | 6.292 | 0.00049757 | 6.3196 |  | 10.3196 | 4 | 10.3196 | 39.4973 | 19.7487 | 20 | 20 | -0.25135 | -14.0786
1353 | 22.55 | 1.9971 | 10.3908 | 2 | 10.4 | 39.5032 | 0 | 0.0091825 | 125.8495 | 0.00016394 | 0.027548 | 6.2925 | 0.00049181 | 6.3205 |  | 10.3205 | 4 | 10.3205 | 39.5032 | 19.7516 | 20 | 20 | -0.24839 | -14.327
1354 | 22.5667 | 1.9971 | 10.3907 | 2 | 10.4 | 39.5091 | 0 | 0.0093445 | 125.8588 | 0.00016201 | 0.028034 | 6.2929 | 0.00048603 | 6.3215 |  | 10.3215 | 4 | 10.3215 | 39.5091 | 19.7546 | 20 | 20 | -0.24543 | -14.5725
1355 | 22.5833 | 1.997 | 10.3905 | 2 | 10.4 | 39.5151 | 0 | 0.0095046 | 125.8683 | 0.00016008 | 0.028514 | 6.2934 | 0.00048023 | 6.3224 |  | 10.3224 | 4 | 10.3224 | 39.5151 | 19.7575 | 20 | 20 | -0.24246 | -14.8149
1356 | 22.6 | 1.997 | 10.3903 | 2 | 10.4 | 39.521 | 0 | 0.0096627 | 125.878 | 0.00015814 | 0.028988 | 6.2939 | 0.00047443 | 6.3234 |  | 10.3234 | 4 | 10.3234 | 39.521 | 19.7605 | 20 | 20 | -0.23949 | -15.0544
1357 | 22.6167 | 1.9969 | 10.3902 | 2 | 10.4 | 39.527 | 0 | 0.0098189 | 125.8878 | 0.0001562 | 0.029457 | 6.2944 | 0.00046861 | 6.3243 |  | 10.3243 | 4 | 10.3243 | 39.527 | 19.7635 | 20 | 20 | -0.23651 | -15.2909
1358 | 22.6333 | 1.9969 | 10.39 | 2 | 10.4 | 39.533 | 0 | 0.0099732 | 125.8978 | 0.00015426 | 0.02992 | 6.2949 | 0.00046278 | 6.3253 |  | 10.3253 | 4 | 10.3253 | 39.533 | 19.7665 | 20 | 20 | -0.23352 | -15.5245
1359 | 22.65 | 1.9968 | 10.3899 | 2 | 10.4 | 39.5389 | 0 | 0.010126 | 125.9079 | 0.00015231 | 0.030377 | 6.2954 | 0.00045693 | 6.3262 |  | 10.3262 | 4 | 10.3262 | 39.5389 | 19.7695 | 20 | 20 | -0.23053 | -15.755
1360 | 22.6667 | 1.9968 | 10.3897 | 2 | 10.4 | 39.5449 | 0 | 0.010276 | 125.9182 | 0.00015036 | 0.030828 | 6.2959 | 0.00045108 | 6.3272 |  | 10.3272 | 4 | 10.3272 | 39.5449 | 19.7725 | 20 | 20 | -0.22754 | -15.9825
1361 | 22.6833 | 1.9967 | 10.3896 | 2 | 10.4 | 39.5509 | 0 | 0.010424 | 125.9286 | 0.00014841 | 0.031273 | 6.2964 | 0.00044522 | 6.3281 |  | 10.3281 | 4 | 10.3281 | 39.5509 | 19.7755 | 20 | 20 | -0.22453 | -16.2071
1362 | 22.7 | 1.9967 | 10.3894 | 2 | 10.4 | 39.5569 | 0 | 0.010571 | 125.9392 | 0.00014645 | 0.031712 | 6.297 | 0.00043934 | 6.3291 |  | 10.3291 | 4 | 10.3291 | 39.5569 | 19.7785 | 20 | 20 | -0.22153 | -16.4286
1363 | 22.7167 | 1.9967 | 10.3893 | 2 | 10.4 | 39.563 | 0 | 0.010715 | 125.9499 | 0.00014449 | 0.032146 | 6.2975 | 0.00043346 | 6.3301 |  | 10.3301 | 4 | 10.3301 | 39.563 | 19.7815 | 20 | 20 | -0.21852 | -16.6471
1364 | 22.7333 | 1.9966 | 10.3891 | 2 | 10.4 | 39.569 | 0 | 0.010858 | 125.9608 | 0.00014252 | 0.032573 | 6.298 | 0.00042757 | 6.331 |  | 10.331 | 4 | 10.331 | 39.569 | 19.7845 | 20 | 20 | -0.2155 | -16.8626
1365 | 22.75 | 1.9966 | 10.389 | 2 | 10.4 | 39.575 | 0 | 0.010998 | 125.9718 | 0.00014056 | 0.032995 | 6.2986 | 0.00042167 | 6.332 |  | 10.332 | 4 | 10.332 | 39.575 | 19.7875 | 20 | 20 | -0.21248 | -17.0751
1366 | 22.7667 | 1.9965 | 10.3889 | 2 | 10.4 | 39.5811 | 0 | 0.011137 | 125.9829 | 0.00013859 | 0.033411 | 6.2991 | 0.00041577 | 6.333 |  | 10.333 | 4 | 10.333 | 39.5811 | 19.7905 | 20 | 20 | -0.20946 | -17.2846
1367 | 22.7833 | 1.9965 | 10.3887 | 2 | 10.4 | 39.5871 | 0 | 0.011273 | 125.9942 | 0.00013662 | 0.03382 | 6.2997 | 0.00040985 | 6.3339 |  | 10.3339 | 4 | 10.3339 | 39.5871 | 19.7936 | 20 | 20 | -0.20644 | -17.491
1368 | 22.8 | 1.9964 | 10.3886 | 2 | 10.4 | 39.5932 | 0 | 0.011408 | 126.0056 | 0.00013465 | 0.034224 | 6.3003 | 0.00040394 | 6.3349 |  | 10.3349 | 4 | 10.3349 | 39.5932 | 19.7966 | 20 | 20 | -0.20341 | -17.6944
1369 | 22.8167 | 1.9964 | 10.3885 | 2 | 10.4 | 39.5992 | 0 | 0.011541 | 126.0171 | 0.00013267 | 0.034622 | 6.3009 | 0.00039802 | 6.3359 |  | 10.3359 | 4 | 10.3359 | 39.5992 | 19.7996 | 20 | 20 | -0.20038 | -17.8948
1370 | 22.8333 | 1.9964 | 10.3883 | 2 | 10.4 | 39.6053 | 0 | 0.011672 | 126.0288 | 0.0001307 | 0.035015 | 6.3014 | 0.00039209 | 6.3368 |  | 10.3368 | 4 | 10.3368 | 39.6053 | 19.8026 | 20 | 20 | -0.19735 | -18.0922
1371 | 22.85 | 1.9963 | 10.3882 | 2 | 10.4 | 39.6114 | 0 | 0.0118 | 126.0406 | 0.00012872 | 0.035401 | 6.302 | 0.00038616 | 6.3378 |  | 10.3378 | 4 | 10.3378 | 39.6114 | 19.8057 | 20 | 20 | -0.19432 | -18.2865
1372 | 22.8667 | 1.9963 | 10.3881 | 2 | 10.4 | 39.6174 | 0 | 0.011927 | 126.0525 | 0.00012674 | 0.035781 | 6.3026 | 0.00038023 | 6.3388 |  | 10.3388 | 4 | 10.3388 | 39.6174 | 19.8087 | 20 | 20 | -0.19129 | -18.4778
1373 | 22.8833 | 1.9962 | 10.3879 | 2 | 10.4 | 39.6235 | 0 | 0.012052 | 126.0646 | 0.00012476 | 0.036155 | 6.3032 | 0.00037429 | 6.3398 |  | 10.3398 | 4 | 10.3398 | 39.6235 | 19.8117 | 20 | 20 | -0.18825 | -18.666
1374 | 22.9 | 1.9962 | 10.3878 | 2 | 10.4 | 39.6296 | 0 | 0.012175 | 126.0768 | 0.00012279 | 0.036524 | 6.3038 | 0.00036836 | 6.3407 |  | 10.3407 | 4 | 10.3407 | 39.6296 | 19.8148 | 20 | 20 | -0.18522 | -18.8512
1375 | 22.9167 | 1.9962 | 10.3877 | 2 | 10.4 | 39.6356 | 0 | 0.012295 | 126.089 | 0.00012081 | 0.036886 | 6.3045 | 0.00036242 | 6.3417 |  | 10.3417 | 4 | 10.3417 | 39.6356 | 19.8178 | 20 | 20 | -0.18219 | -19.0334
1376 | 22.9333 | 1.9961 | 10.3876 | 2 | 10.4 | 39.6417 | 0 | 0.012414 | 126.1015 | 0.00011883 | 0.037242 | 6.3051 | 0.00035648 | 6.3427 |  | 10.3427 | 4 | 10.3427 | 39.6417 | 19.8209 | 20 | 20 | -0.17915 | -19.2126
1377 | 22.95 | 1.9961 | 10.3875 | 2 | 10.4 | 39.6478 | 0 | 0.012531 | 126.114 | 0.00011685 | 0.037593 | 6.3057 | 0.00035054 | 6.3436 |  | 10.3436 | 4 | 10.3436 | 39.6478 | 19.8239 | 20 | 20 | -0.17612 | -19.3887
1378 | 22.9667 | 1.996 | 10.3874 | 2 | 10.4 | 39.6538 | 0 | 0.012646 | 126.1266 | 0.00011487 | 0.037938 | 6.3063 | 0.0003446 | 6.3446 |  | 10.3446 | 4 | 10.3446 | 39.6538 | 19.8269 | 20 | 20 | -0.17308 | -19.5618
1379 | 22.9833 | 1.996 | 10.3872 | 2 | 10.4 | 39.6599 | 0 | 0.012759 | 126.1394 | 0.00011289 | 0.038276 | 6.307 | 0.00033867 | 6.3456 |  | 10.3456 | 4 | 10.3456 | 39.6599 | 19.83 | 20 | 20 | -0.17005 | -19.7318
1380 | 23 | 1.996 | 10.3871 | 2 | 10.4 | 39.666 | 0 | 0.01287 | 126.1523 | 0.00011091 | 0.038609 | 6.3076 | 0.00033273 | 6.3466 |  | 10.3466 | 4 | 10.3466 | 39.666 | 19.833 | 20 | 20 | -0.16702 | -19.8988
1381 | 23.0167 | 1.9959 | 10.387 | 2 | 10.4 | 39.672 | 0 | 0.012979 | 126.1652 | 0.00010893 | 0.038936 | 6.3083 | 0.0003268 | 6.3475 |  | 10.3475 | 4 | 10.3475 | 39.672 | 19.836 | 20 | 20 | -0.16398 | -20.0628
1382 | 23.0333 | 1.9959 | 10.3869 | 2 | 10.4 | 39.6781 | 0 | 0.013086 | 126.1783 | 0.00010696 | 0.039257 | 6.3089 | 0.00032087 | 6.3485 |  | 10.3485 | 4 | 10.3485 | 39.6781 | 19.839 | 20 | 20 | -0.16096 | -20.2238
1383 | 23.05 | 1.9959 | 10.3868 | 2 | 10.4 | 39.6841 | 0 | 0.013191 | 126.1915 | 0.00010498 | 0.039572 | 6.3096 | 0.00031494 | 6.3495 |  | 10.3495 | 4 | 10.3495 | 39.6841 | 19.8421 | 20 | 20 | -0.15793 | -20.3817
1384 | 23.0667 | 1.9958 | 10.3867 | 2 | 10.4 | 39.6902 | 0 | 0.013294 | 126.2048 | 0.00010301 | 0.039881 | 6.3102 | 0.00030902 | 6.3504 |  | 10.3504 | 4 | 10.3504 | 39.6902 | 19.8451 | 20 | 20 | -0.1549 | -20.5366
1385 | 23.0833 | 1.9958 | 10.3866 | 2 | 10.4 | 39.6962 | 0 | 0.013395 | 126.2182 | 0.00010103 | 0.040184 | 6.3109 | 0.0003031 | 6.3514 |  | 10.3514 | 4 | 10.3514 | 39.6962 | 19.8481 | 20 | 20 | -0.15188 | -20.6885
1386 | 23.1 | 1.9958 | 10.3865 | 2 | 10.4 | 39.7023 | 0 | 0.013494 | 126.2317 | 9.9063e-05 | 0.040481 | 6.3116 | 0.00029719 | 6.3524 |  | 10.3524 | 4 | 10.3524 | 39.7023 | 19.8511 | 20 | 20 | -0.14886 | -20.8374
1387 | 23.1167 | 1.9958 | 10.3864 | 2 | 10.4 | 39.7083 | 0 | 0.013591 | 126.2453 | 9.7094e-05 | 0.040772 | 6.3123 | 0.00029128 | 6.3533 |  | 10.3533 | 4 | 10.3533 | 39.7083 | 19.8542 | 20 | 20 | -0.14585 | -20.9832
1388 | 23.1333 | 1.9957 | 10.3863 | 2 | 10.4 | 39.7143 | 0 | 0.013686 | 126.259 | 9.5127e-05 | 0.041058 | 6.3129 | 0.00028538 | 6.3543 |  | 10.3543 | 4 | 10.3543 | 39.7143 | 19.8572 | 20 | 20 | -0.14284 | -21.126
1389 | 23.15 | 1.9957 | 10.3862 | 2 | 10.4 | 39.7203 | 0 | 0.013779 | 126.2728 | 9.3163e-05 | 0.041337 | 6.3136 | 0.00027949 | 6.3553 |  | 10.3553 | 4 | 10.3553 | 39.7203 | 19.8602 | 20 | 20 | -0.13983 | -21.2659
1390 | 23.1667 | 1.9957 | 10.3861 | 2 | 10.4 | 39.7263 | 0 | 0.01387 | 126.2866 | 9.1201e-05 | 0.041611 | 6.3143 | 0.0002736 | 6.3562 |  | 10.3562 | 4 | 10.3562 | 39.7263 | 19.8632 | 20 | 20 | -0.13683 | -21.4027
1391 | 23.1833 | 1.9956 | 10.386 | 2 | 10.4 | 39.7323 | 0 | 0.013959 | 126.3006 | 8.9242e-05 | 0.041878 | 6.315 | 0.00026773 | 6.3572 |  | 10.3572 | 4 | 10.3572 | 39.7323 | 19.8662 | 20 | 20 | -0.13383 | -21.5365
1392 | 23.2 | 1.9956 | 10.386 | 2 | 10.4 | 39.7383 | 0 | 0.014047 | 126.3146 | 8.7285e-05 | 0.04214 | 6.3157 | 0.00026186 | 6.3581 |  | 10.3581 | 4 | 10.3581 | 39.7383 | 19.8692 | 20 | 20 | -0.13083 | -21.6674
1393 | 23.2167 | 1.9956 | 10.3859 | 2 | 10.4 | 39.7443 | 0 | 0.014132 | 126.3288 | 8.5332e-05 | 0.042396 | 6.3164 | 0.000256 | 6.3591 |  | 10.3591 | 4 | 10.3591 | 39.7443 | 19.8722 | 20 | 20 | -0.12784 | -21.7952
1394 | 23.2333 | 1.9956 | 10.3858 | 2 | 10.4 | 39.7503 | 0 | 0.014215 | 126.343 | 8.3382e-05 | 0.042646 | 6.3171 | 0.00025015 | 6.36 |  | 10.36 | 4 | 10.36 | 39.7503 | 19.8751 | 20 | 20 | -0.12486 | -21.9201
1395 | 23.25 | 1.9955 | 10.3857 | 2 | 10.4 | 39.7562 | 0 | 0.014297 | 126.3573 | 8.1435e-05 | 0.042891 | 6.3179 | 0.00024431 | 6.361 |  | 10.361 | 4 | 10.361 | 39.7562 | 19.8781 | 20 | 20 | -0.12188 | -22.0419
1396 | 23.2667 | 1.9955 | 10.3856 | 2 | 10.4 | 39.7622 | 0 | 0.014376 | 126.3717 | 7.9492e-05 | 0.043129 | 6.3186 | 0.00023848 | 6.362 |  | 10.362 | 4 | 10.362 | 39.7622 | 19.8811 | 20 | 20 | -0.1189 | -22.1608
1397 | 23.2833 | 1.9955 | 10.3855 | 2 | 10.4 | 39.7681 | 0 | 0.014454 | 126.3861 | 7.7553e-05 | 0.043362 | 6.3193 | 0.00023266 | 6.3629 |  | 10.3629 | 4 | 10.3629 | 39.7681 | 19.8841 | 20 | 20 | -0.11594 | -22.2768
1398 | 23.3 | 1.9955 | 10.3855 | 2 | 10.4 | 39.774 | 0 | 0.01453 | 126.4006 | 7.5618e-05 | 0.043589 | 6.32 | 0.00022685 | 6.3638 |  | 10.3638 | 4 | 10.3638 | 39.774 | 19.887 | 20 | 20 | -0.11298 | -22.3897
1399 | 23.3167 | 1.9954 | 10.3854 | 2 | 10.4 | 39.78 | 0 | 0.014603 | 126.4152 | 7.3687e-05 | 0.04381 | 6.3208 | 0.00022106 | 6.3648 |  | 10.3648 | 4 | 10.3648 | 39.78 | 19.89 | 20 | 20 | -0.11002 | -22.4998
1400 | 23.3333 | 1.9954 | 10.3853 | 2 | 10.4 | 39.7859 | 0 | 0.014675 | 126.4299 | 7.176e-05 | 0.044025 | 6.3215 | 0.00021528 | 6.3657 |  | 10.3657 | 4 | 10.3657 | 39.7859 | 19.8929 | 20 | 20 | -0.10707 | -22.6068
1401 | 23.35 | 1.9954 | 10.3853 | 2 | 10.4 | 39.7917 | 0 | 0.014745 | 126.4447 | 6.9837e-05 | 0.044235 | 6.3222 | 0.00020951 | 6.3667 |  | 10.3667 | 4 | 10.3667 | 39.7917 | 19.8959 | 20 | 20 | -0.10413 | -22.711
1402 | 23.3667 | 1.9954 | 10.3852 | 2 | 10.4 | 39.7976 | 0 | 0.014813 | 126.4595 | 6.7919e-05 | 0.044438 | 6.323 | 0.00020376 | 6.3676 |  | 10.3676 | 4 | 10.3676 | 39.7976 | 19.8988 | 20 | 20 | -0.1012 | -22.8122
1403 | 23.3833 | 1.9954 | 10.3851 | 2 | 10.4 | 39.8035 | 0 | 0.014879 | 126.4744 | 6.6006e-05 | 0.044636 | 6.3237 | 0.00019802 | 6.3686 |  | 10.3686 | 4 | 10.3686 | 39.8035 | 19.9017 | 20 | 20 | -0.098275 | -22.9105
1404 | 23.4 | 1.9953 | 10.3851 | 2 | 10.4 | 39.8093 | 0 | 0.014943 | 126.4893 | 6.4098e-05 | 0.044829 | 6.3245 | 0.00019229 | 6.3695 |  | 10.3695 | 4 | 10.3695 | 39.8093 | 19.9046 | 20 | 20 | -0.095357 | -23.0058
1405 | 23.4167 | 1.9953 | 10.385 | 2 | 10.4 | 39.8151 | 0 | 0.015005 | 126.5043 | 6.2195e-05 | 0.045015 | 6.3252 | 0.00018658 | 6.3704 |  | 10.3704 | 4 | 10.3704 | 39.8151 | 19.9076 | 20 | 20 | -0.092447 | -23.0983
1406 | 23.4333 | 1.9953 | 10.3849 | 2 | 10.4 | 39.8209 | 0 | 0.015065 | 126.5194 | 6.0297e-05 | 0.045196 | 6.326 | 0.00018089 | 6.3713 |  | 10.3713 | 4 | 10.3713 | 39.8209 | 19.9105 | 20 | 20 | -0.089546 | -23.1878
1407 | 23.45 | 1.9953 | 10.3849 | 2 | 10.4 | 39.8267 | 0 | 0.015124 | 126.5345 | 5.8404e-05 | 0.045371 | 6.3267 | 0.00017521 | 6.3723 |  | 10.3723 | 4 | 10.3723 | 39.8267 | 19.9133 | 20 | 20 | -0.086653 | -23.2745
1408 | 23.4667 | 1.9953 | 10.3848 | 2 | 10.4 | 39.8325 | 0 | 0.01518 | 126.5497 | 5.6518e-05 | 0.045541 | 6.3275 | 0.00016955 | 6.3732 |  | 10.3732 | 4 | 10.3732 | 39.8325 | 19.9162 | 20 | 20 | -0.083769 | -23.3582
1409 | 23.4833 | 1.9952 | 10.3848 | 2 | 10.4 | 39.8382 | 0 | 0.015235 | 126.5649 | 5.4636e-05 | 0.045705 | 6.3282 | 0.00016391 | 6.3741 |  | 10.3741 | 4 | 10.3741 | 39.8382 | 19.9191 | 20 | 20 | -0.080894 | -23.4391
1410 | 23.5 | 1.9952 | 10.3847 | 2 | 10.4 | 39.8439 | 0 | 0.015288 | 126.5802 | 5.2761e-05 | 0.045863 | 6.329 | 0.00015828 | 6.375 |  | 10.375 | 4 | 10.375 | 39.8439 | 19.922 | 20 | 20 | -0.078028 | -23.5171
1411 | 23.5167 | 1.9952 | 10.3847 | 2 | 10.4 | 39.8497 | 0 | 0.015339 | 126.5955 | 5.0892e-05 | 0.046016 | 6.3298 | 0.00015268 | 6.3759 |  | 10.3759 | 4 | 10.3759 | 39.8497 | 19.9248 | 20 | 20 | -0.075172 | -23.5923
1412 | 23.5333 | 1.9952 | 10.3846 | 2 | 10.4 | 39.8553 | 0 | 0.015388 | 126.6109 | 4.9029e-05 | 0.046163 | 6.3305 | 0.00014709 | 6.3769 |  | 10.3769 | 4 | 10.3769 | 39.8553 | 19.9277 | 20 | 20 | -0.072325 | -23.6646
1413 | 23.55 | 1.9952 | 10.3846 | 2 | 10.4 | 39.861 | 0 | 0.015435 | 126.6264 | 4.7173e-05 | 0.046304 | 6.3313 | 0.00014152 | 6.3778 |  | 10.3778 | 4 | 10.3778 | 39.861 | 19.9305 | 20 | 20 | -0.069489 | -23.7341
1414 | 23.5667 | 1.9952 | 10.3845 | 2 | 10.4 | 39.8667 | 0 | 0.01548 | 126.6418 | 4.5323e-05 | 0.04644 | 6.3321 | 0.00013597 | 6.3787 |  | 10.3787 | 4 | 10.3787 | 39.8667 | 19.9333 | 20 | 20 | -0.066662 | -23.8008
1415 | 23.5833 | 1.9951 | 10.3845 | 2 | 10.4 | 39.8723 | 0 | 0.015524 | 126.6574 | 4.3479e-05 | 0.046571 | 6.3329 | 0.00013044 | 6.3796 |  | 10.3796 | 4 | 10.3796 | 39.8723 | 19.9362 | 20 | 20 | -0.063846 | -23.8646
1416 | 23.6 | 1.9951 | 10.3844 | 2 | 10.4 | 39.8779 | 0 | 0.015565 | 126.6729 | 4.1643e-05 | 0.046696 | 6.3336 | 0.00012493 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8779 | 19.939 | 20 | 20 | -0.061041 | -23.9257
1417 | 23.6167 | 1.9951 | 10.3844 | 2 | 10.4 | 39.8835 | 0 | 0.015605 | 126.6885 | 3.9813e-05 | 0.046815 | 6.3344 | 0.00011944 | 6.3814 |  | 10.3814 | 4 | 10.3814 | 39.8835 | 19.9418 | 20 | 20 | -0.058247 | -23.9839
1418 | 23.6333 | 1.9951 | 10.3844 | 2 | 10.4 | 39.8891 | 0 | 0.015643 | 126.7042 | 3.799e-05 | 0.046929 | 6.3352 | 0.00011397 | 6.3823 |  | 10.3823 | 4 | 10.3823 | 39.8891 | 19.9445 | 20 | 20 | -0.055464 | -24.0394
1419 | 23.65 | 1.9951 | 10.3843 | 2 | 10.4 | 39.8946 | 0 | 0.015679 | 126.7199 | 3.6175e-05 | 0.047038 | 6.336 | 0.00010852 | 6.3831 |  | 10.3831 | 4 | 10.3831 | 39.8946 | 19.9473 | 20 | 20 | -0.052692 | -24.0921
1420 | 23.6667 | 1.9951 | 10.3843 | 2 | 10.4 | 39.9001 | 0 | 0.015714 | 126.7356 | 3.4367e-05 | 0.047141 | 6.3368 | 0.0001031 | 6.384 |  | 10.384 | 4 | 10.384 | 39.9001 | 19.9501 | 20 | 20 | -0.049931 | -24.142
1421 | 23.6833 | 1.9951 | 10.3843 | 2 | 10.4 | 39.9056 | 0 | 0.015746 | 126.7513 | 3.2567e-05 | 0.047238 | 6.3376 | 9.77e-05 | 6.3849 |  | 10.3849 | 4 | 10.3849 | 39.9056 | 19.9528 | 20 | 20 | -0.047182 | -24.1892
1422 | 23.7 | 1.9951 | 10.3842 | 2 | 10.4 | 39.9111 | 0 | 0.015777 | 126.7671 | 3.0774e-05 | 0.047331 | 6.3384 | 9.2321e-05 | 6.3858 |  | 10.3858 | 4 | 10.3858 | 39.9111 | 19.9556 | 20 | 20 | -0.044445 | -24.2336
1423 | 23.7167 | 1.9951 | 10.3842 | 2 | 10.4 | 39.9166 | 0 | 0.015806 | 126.7829 | 2.8989e-05 | 0.047418 | 6.3391 | 8.6966e-05 | 6.3866 |  | 10.3866 | 4 | 10.3866 | 39.9166 | 19.9583 | 20 | 20 | -0.041721 | -24.2754
1424 | 23.7333 | 1.9951 | 10.3842 | 2 | 10.4 | 39.922 | 0 | 0.015833 | 126.7987 | 2.7211e-05 | 0.047499 | 6.3399 | 8.1634e-05 | 6.3875 |  | 10.3875 | 4 | 10.3875 | 39.922 | 19.961 | 20 | 20 | -0.039008 | -24.3144
1425 | 23.75 | 1.995 | 10.3841 | 2 | 10.4 | 39.9274 | 0 | 0.015859 | 126.8146 | 2.5442e-05 | 0.047576 | 6.3407 | 7.6327e-05 | 6.3884 |  | 10.3884 | 4 | 10.3884 | 39.9274 | 19.9637 | 20 | 20 | -0.036309 | -24.3507
1426 | 23.7667 | 1.995 | 10.3841 | 2 | 10.4 | 39.9328 | 0 | 0.015882 | 126.8305 | 2.3681e-05 | 0.047647 | 6.3415 | 7.1044e-05 | 6.3892 |  | 10.3892 | 4 | 10.3892 | 39.9328 | 19.9664 | 20 | 20 | -0.033621 | -24.3843
1427 | 23.7833 | 1.995 | 10.3841 | 2 | 10.4 | 39.9381 | 0 | 0.015904 | 126.8464 | 2.1929e-05 | 0.047712 | 6.3423 | 6.5787e-05 | 6.3901 |  | 10.3901 | 4 | 10.3901 | 39.9381 | 19.9691 | 20 | 20 | -0.030947 | -24.4152
1428 | 23.8 | 1.995 | 10.3841 | 2 | 10.4 | 39.9434 | 0 | 0.015924 | 126.8623 | 2.0185e-05 | 0.047773 | 6.3431 | 6.0554e-05 | 6.3909 |  | 10.3909 | 4 | 10.3909 | 39.9434 | 19.9717 | 20 | 20 | -0.028286 | -24.4435
1429 | 23.8167 | 1.995 | 10.3841 | 2 | 10.4 | 39.9487 | 0 | 0.015943 | 126.8782 | 1.8449e-05 | 0.047828 | 6.3439 | 5.5347e-05 | 6.3918 |  | 10.3918 | 4 | 10.3918 | 39.9487 | 19.9744 | 20 | 20 | -0.025638 | -24.4692
1430 | 23.8333 | 1.995 | 10.384 | 2 | 10.4 | 39.954 | 0 | 0.01596 | 126.8942 | 1.6722e-05 | 0.047879 | 6.3447 | 5.0166e-05 | 6.3926 |  | 10.3926 | 4 | 10.3926 | 39.954 | 19.977 | 20 | 20 | -0.023004 | -24.4922
1431 | 23.85 | 1.995 | 10.384 | 2 | 10.4 | 39.9592 | 0 | 0.015975 | 126.9102 | 1.5004e-05 | 0.047924 | 6.3455 | 4.5012e-05 | 6.3935 |  | 10.3935 | 4 | 10.3935 | 39.9592 | 19.9796 | 20 | 20 | -0.020384 | -24.5126
1432 | 23.8667 | 1.995 | 10.384 | 2 | 10.4 | 39.9644 | 0 | 0.015988 | 126.9262 | 1.3295e-05 | 0.047963 | 6.3463 | 3.9884e-05 | 6.3943 |  | 10.3943 | 4 | 10.3943 | 39.9644 | 19.9822 | 20 | 20 | -0.017777 | -24.5303
1433 | 23.8833 | 1.995 | 10.384 | 2 | 10.4 | 39.9696 | 0 | 0.015999 | 126.9422 | 1.1595e-05 | 0.047998 | 6.3471 | 3.4784e-05 | 6.3951 |  | 10.3951 | 4 | 10.3951 | 39.9696 | 19.9848 | 20 | 20 | -0.015184 | -24.5455
1434 | 23.9 | 1.995 | 10.384 | 2 | 10.4 | 39.9748 | 0 | 0.016009 | 126.9582 | 9.9036e-06 | 0.048028 | 6.3479 | 2.9711e-05 | 6.396 |  | 10.396 | 4 | 10.396 | 39.9748 | 19.9874 | 20 | 20 | -0.012606 | -24.5581
1435 | 23.9167 | 1.995 | 10.384 | 2 | 10.4 | 39.9799 | 0 | 0.016018 | 126.9742 | 8.2219e-06 | 0.048053 | 6.3487 | 2.4666e-05 | 6.3968 |  | 10.3968 | 4 | 10.3968 | 39.9799 | 19.99 | 20 | 20 | -0.010042 | -24.5682
1436 | 23.9333 | 1.995 | 10.384 | 2 | 10.4 | 39.985 | 0 | 0.016024 | 126.9902 | 6.5495e-06 | 0.048072 | 6.3495 | 1.9649e-05 | 6.3976 |  | 10.3976 | 4 | 10.3976 | 39.985 | 19.9925 | 20 | 20 | -0.0074923 | -24.5757
1437 | 23.95 | 1.995 | 10.384 | 2 | 10.4 | 39.9901 | 0 | 0.016029 | 127.0062 | 4.8867e-06 | 0.048087 | 6.3503 | 1.466e-05 | 6.3984 |  | 10.3984 | 4 | 10.3984 | 39.9901 | 19.995 | 20 | 20 | -0.0049575 | -24.5806
1438 | 23.9667 | 1.995 | 10.384 | 2 | 10.4 | 39.9951 | 0 | 0.016032 | 127.0223 | 3.2334e-06 | 0.048097 | 6.3511 | 9.7003e-06 | 6.3992 |  | 10.3992 | 4 | 10.3992 | 39.9951 | 19.9976 | 20 | 20 | -0.0024377 | -24.5831
1439 | 23.9833 | 1.995 | 10.384 | 2 | 10.4 | 40.0001 | 0 | 0.016034 | 127.0383 | 1.5899e-06 | 0.048101 | 6.3519 | 4.7698e-06 | 6.4 |  | 10.4 | 4 | 10.4 | 40.0001 | 20.0001 | 20 | 20 | 6.7105e-05 | -24.583
1440 | 24 | 1.995 | 10.384 | 2 | 10.4 | 40.0051 | 0 | 0.016034 | 127.0543 | -4.3768e-08 | 0.048101 | 6.3527 | -1.313e-07 | 6.4008 |  | 10.4008 | 4 | 10.4008 | 40.0051 | 20.0026 | 20 | 20 | 0.0025567 | -24.5804
1441 | 24.0167 | 1.995 | 10.384 | 2 | 10.4 | 40.0101 | 0 | 0.016032 | 127.0704 | -1.6675e-06 | 0.048096 | 6.3535 | -5.0026e-06 | 6.4016 |  | 10.4016 | 4 | 10.4016 | 40.0101 | 20.005 | 20 | 20 | 0.0050308 | -24.5754
1442 | 24.0333 | 1.995 | 10.384 | 2 | 10.4 | 40.015 | 0 | 0.016029 | 127.0864 | -3.2812e-06 | 0.048086 | 6.3543 | -9.8437e-06 | 6.4024 |  | 10.4024 | 4 | 10.4024 | 40.015 | 20.0075 | 20 | 20 | 0.0074894 | -24.5679
1443 | 24.05 | 1.995 | 10.384 | 2 | 10.4 | 40.0199 | 0 | 0.016024 | 127.1024 | -4.8848e-06 | 0.048072 | 6.3551 | -1.4654e-05 | 6.4032 |  | 10.4032 | 4 | 10.4032 | 40.0199 | 20.0099 | 20 | 20 | 0.0099323 | -24.558
1444 | 24.0667 | 1.995 | 10.384 | 2 | 10.4 | 40.0247 | 0 | 0.016017 | 127.1184 | -6.4782e-06 | 0.048052 | 6.3559 | -1.9434e-05 | 6.404 |  | 10.404 | 4 | 10.404 | 40.0247 | 20.0124 | 20 | 20 | 0.012359 | -24.5456
1445 | 24.0833 | 1.995 | 10.384 | 2 | 10.4 | 40.0295 | 0 | 0.016009 | 127.1345 | -8.0611e-06 | 0.048028 | 6.3567 | -2.4183e-05 | 6.4047 |  | 10.4047 | 4 | 10.4047 | 40.0295 | 20.0148 | 20 | 20 | 0.01477 | -24.5309
1446 | 24.1 | 1.995 | 10.384 | 2 | 10.4 | 40.0343 | 0 | 0.016 | 127.1505 | -9.6337e-06 | 0.047999 | 6.3575 | -2.8901e-05 | 6.4055 |  | 10.4055 | 4 | 10.4055 | 40.0343 | 20.0172 | 20 | 20 | 0.017165 | -24.5137
1447 | 24.1167 | 1.995 | 10.384 | 2 | 10.4 | 40.0391 | 0 | 0.015989 | 127.1664 | -1.1196e-05 | 0.047966 | 6.3583 | -3.3587e-05 | 6.4063 |  | 10.4063 | 4 | 10.4063 | 40.0391 | 20.0195 | 20 | 20 | 0.019544 | -24.4941
1448 | 24.1333 | 1.995 | 10.384 | 2 | 10.4 | 40.0438 | 0 | 0.015976 | 127.1824 | -1.2747e-05 | 0.047927 | 6.3591 | -3.8241e-05 | 6.407 |  | 10.407 | 4 | 10.407 | 40.0438 | 20.0219 | 20 | 20 | 0.021906 | -24.4722
1449 | 24.15 | 1.995 | 10.384 | 2 | 10.4 | 40.0485 | 0 | 0.015962 | 127.1984 | -1.4288e-05 | 0.047885 | 6.3599 | -4.2863e-05 | 6.4078 |  | 10.4078 | 4 | 10.4078 | 40.0485 | 20.0243 | 20 | 20 | 0.024252 | -24.448
1450 | 24.1667 | 1.995 | 10.3841 | 2 | 10.4 | 40.0532 | 0 | 0.015946 | 127.2143 | -1.5818e-05 | 0.047837 | 6.3607 | -4.7453e-05 | 6.4085 |  | 10.4085 | 4 | 10.4085 | 40.0532 | 20.0266 | 20 | 20 | 0.026581 | -24.4214
1451 | 24.1833 | 1.995 | 10.3841 | 2 | 10.4 | 40.0578 | 0 | 0.015928 | 127.2303 | -1.7337e-05 | 0.047785 | 6.3615 | -5.201e-05 | 6.4092 |  | 10.4092 | 4 | 10.4092 | 40.0578 | 20.0289 | 20 | 20 | 0.028893 | -24.3925
1452 | 24.2 | 1.995 | 10.3841 | 2 | 10.4 | 40.0624 | 0 | 0.01591 | 127.2462 | -1.8845e-05 | 0.047729 | 6.3623 | -5.6534e-05 | 6.41 |  | 10.41 | 4 | 10.41 | 40.0624 | 20.0312 | 20 | 20 | 0.031188 | -24.3613
1453 | 24.2167 | 1.995 | 10.3841 | 2 | 10.4 | 40.0669 | 0 | 0.015889 | 127.2621 | -2.0342e-05 | 0.047668 | 6.3631 | -6.1025e-05 | 6.4107 |  | 10.4107 | 4 | 10.4107 | 40.0669 | 20.0335 | 20 | 20 | 0.033466 | -24.3279
1454 | 24.2333 | 1.995 | 10.3841 | 2 | 10.4 | 40.0715 | 0 | 0.015867 | 127.2779 | -2.1827e-05 | 0.047602 | 6.3639 | -6.5482e-05 | 6.4114 |  | 10.4114 | 4 | 10.4114 | 40.0715 | 20.0357 | 20 | 20 | 0.035726 | -24.2921
1455 | 24.25 | 1.995 | 10.3842 | 2 | 10.4 | 40.0759 | 0 | 0.015844 | 127.2938 | -2.3302e-05 | 0.047532 | 6.3647 | -6.9905e-05 | 6.4122 |  | 10.4122 | 4 | 10.4122 | 40.0759 | 20.038 | 20 | 20 | 0.03797 | -24.2542
1456 | 24.2667 | 1.9951 | 10.3842 | 2 | 10.4 | 40.0804 | 0 | 0.015819 | 127.3096 | -2.4765e-05 | 0.047458 | 6.3655 | -7.4295e-05 | 6.4129 |  | 10.4129 | 4 | 10.4129 | 40.0804 | 20.0402 | 20 | 20 | 0.040196 | -24.214
1457 | 24.2833 | 1.9951 | 10.3842 | 2 | 10.4 | 40.0848 | 0 | 0.015793 | 127.3254 | -2.6217e-05 | 0.047379 | 6.3663 | -7.865e-05 | 6.4136 |  | 10.4136 | 4 | 10.4136 | 40.0848 | 20.0424 | 20 | 20 | 0.042404 | -24.1716
1458 | 24.3 | 1.9951 | 10.3842 | 2 | 10.4 | 40.0892 | 0 | 0.015765 | 127.3411 | -2.7657e-05 | 0.047296 | 6.3671 | -8.2971e-05 | 6.4143 |  | 10.4143 | 4 | 10.4143 | 40.0892 | 20.0446 | 20 | 20 | 0.044594 | -24.127
1459 | 24.3167 | 1.9951 | 10.3843 | 2 | 10.4 | 40.0935 | 0 | 0.015736 | 127.3569 | -2.9086e-05 | 0.047209 | 6.3678 | -8.7257e-05 | 6.415 |  | 10.415 | 4 | 10.415 | 40.0935 | 20.0468 | 20 | 20 | 0.046767 | -24.0802
1460 | 24.3333 | 1.9951 | 10.3843 | 2 | 10.4 | 40.0978 | 0 | 0.015706 | 127.3726 | -3.0503e-05 | 0.047117 | 6.3686 | -9.1509e-05 | 6.4157 |  | 10.4157 | 4 | 10.4157 | 40.0978 | 20.0489 | 20 | 20 | 0.048922 | -24.0313
1461 | 24.35 | 1.9951 | 10.3843 | 2 | 10.4 | 40.1021 | 0 | 0.015674 | 127.3883 | -3.1908e-05 | 0.047022 | 6.3694 | -9.5725e-05 | 6.4163 |  | 10.4163 | 4 | 10.4163 | 40.1021 | 20.0511 | 20 | 20 | 0.051059 | -23.9802
1462 | 24.3667 | 1.9951 | 10.3844 | 2 | 10.4 | 40.1064 | 0 | 0.015641 | 127.4039 | -3.3302e-05 | 0.046922 | 6.3702 | -9.9906e-05 | 6.417 |  | 10.417 | 4 | 10.417 | 40.1064 | 20.0532 | 20 | 20 | 0.053177 | -23.927
1463 | 24.3833 | 1.9951 | 10.3844 | 2 | 10.4 | 40.1106 | 0 | 0.015606 | 127.4195 | -3.4684e-05 | 0.046818 | 6.371 | -0.00010405 | 6.4177 |  | 10.4177 | 4 | 10.4177 | 40.1106 | 20.0553 | 20 | 20 | 0.055278 | -23.8718
1464 | 24.4 | 1.9951 | 10.3844 | 2 | 10.4 | 40.1147 | 0 | 0.01557 | 127.4351 | -3.6054e-05 | 0.04671 | 6.3718 | -0.00010816 | 6.4184 |  | 10.4184 | 4 | 10.4184 | 40.1147 | 20.0574 | 20 | 20 | 0.057359 | -23.8144
1465 | 24.4167 | 1.9951 | 10.3845 | 2 | 10.4 | 40.1188 | 0 | 0.015532 | 127.4506 | -3.7412e-05 | 0.046597 | 6.3725 | -0.00011223 | 6.419 |  | 10.419 | 4 | 10.419 | 40.1188 | 20.0594 | 20 | 20 | 0.059423 | -23.755
1466 | 24.4333 | 1.9952 | 10.3845 | 2 | 10.4 | 40.1229 | 0 | 0.015494 | 127.4661 | -3.8757e-05 | 0.046481 | 6.3733 | -0.00011627 | 6.4197 |  | 10.4197 | 4 | 10.4197 | 40.1229 | 20.0615 | 20 | 20 | 0.061468 | -23.6935
1467 | 24.45 | 1.9952 | 10.3845 | 2 | 10.4 | 40.127 | 0 | 0.015454 | 127.4816 | -4.0091e-05 | 0.046361 | 6.3741 | -0.00012027 | 6.4203 |  | 10.4203 | 4 | 10.4203 | 40.127 | 20.0635 | 20 | 20 | 0.063494 | -23.63
1468 | 24.4667 | 1.9952 | 10.3846 | 2 | 10.4 | 40.131 | 0 | 0.015412 | 127.497 | -4.1413e-05 | 0.046237 | 6.3748 | -0.00012424 | 6.421 |  | 10.421 | 4 | 10.421 | 40.131 | 20.0655 | 20 | 20 | 0.065502 | -23.5645
1469 | 24.4833 | 1.9952 | 10.3846 | 2 | 10.4 | 40.135 | 0 | 0.015369 | 127.5123 | -4.2722e-05 | 0.046108 | 6.3756 | -0.00012817 | 6.4216 |  | 10.4216 | 4 | 10.4216 | 40.135 | 20.0675 | 20 | 20 | 0.06749 | -23.497
1470 | 24.5 | 1.9952 | 10.3847 | 2 | 10.4 | 40.1389 | 0 | 0.015325 | 127.5277 | -4.4019e-05 | 0.045976 | 6.3764 | -0.00013206 | 6.4222 |  | 10.4222 | 4 | 10.4222 | 40.1389 | 20.0695 | 20 | 20 | 0.06946 | -23.4276
1471 | 24.5167 | 1.9952 | 10.3847 | 2 | 10.4 | 40.1428 | 0 | 0.01528 | 127.5429 | -4.5304e-05 | 0.04584 | 6.3771 | -0.00013591 | 6.4229 |  | 10.4229 | 4 | 10.4229 | 40.1428 | 20.0714 | 20 | 20 | 0.071411 | -23.3562
1472 | 24.5333 | 1.9952 | 10.3848 | 2 | 10.4 | 40.1467 | 0 | 0.015234 | 127.5582 | -4.6576e-05 | 0.045701 | 6.3779 | -0.00013973 | 6.4235 |  | 10.4235 | 4 | 10.4235 | 40.1467 | 20.0733 | 20 | 20 | 0.073343 | -23.2828
1473 | 24.55 | 1.9953 | 10.3848 | 2 | 10.4 | 40.1505 | 0 | 0.015186 | 127.5734 | -4.7836e-05 | 0.045557 | 6.3787 | -0.00014351 | 6.4241 |  | 10.4241 | 4 | 10.4241 | 40.1505 | 20.0753 | 20 | 20 | 0.075255 | -23.2076
1474 | 24.5667 | 1.9953 | 10.3849 | 2 | 10.4 | 40.1543 | 0 | 0.015137 | 127.5885 | -4.9084e-05 | 0.04541 | 6.3794 | -0.00014725 | 6.4247 |  | 10.4247 | 4 | 10.4247 | 40.1543 | 20.0771 | 20 | 20 | 0.077148 | -23.1304
1475 | 24.5833 | 1.9953 | 10.3849 | 2 | 10.4 | 40.158 | 0 | 0.015086 | 127.6036 | -5.0318e-05 | 0.045259 | 6.3802 | -0.00015096 | 6.4253 |  | 10.4253 | 4 | 10.4253 | 40.158 | 20.079 | 20 | 20 | 0.079022 | -23.0514
1476 | 24.6 | 1.9953 | 10.385 | 2 | 10.4 | 40.1618 | 0 | 0.015035 | 127.6186 | -5.1541e-05 | 0.045104 | 6.3809 | -0.00015462 | 6.4259 |  | 10.4259 | 4 | 10.4259 | 40.1618 | 20.0809 | 20 | 20 | 0.080877 | -22.9705
1477 | 24.6167 | 1.9953 | 10.385 | 2 | 10.4 | 40.1654 | 0 | 0.014982 | 127.6336 | -5.275e-05 | 0.044946 | 6.3817 | -0.00015825 | 6.4265 |  | 10.4265 | 4 | 10.4265 | 40.1654 | 20.0827 | 20 | 20 | 0.082712 | -22.8878
1478 | 24.6333 | 1.9953 | 10.3851 | 2 | 10.4 | 40.1691 | 0 | 0.014928 | 127.6485 | -5.3947e-05 | 0.044784 | 6.3824 | -0.00016184 | 6.427 |  | 10.427 | 4 | 10.427 | 40.1691 | 20.0845 | 20 | 20 | 0.084527 | -22.8033
1479 | 24.65 | 1.9954 | 10.3851 | 2 | 10.4 | 40.1726 | 0 | 0.014873 | 127.6634 | -5.5131e-05 | 0.044619 | 6.3832 | -0.00016539 | 6.4276 |  | 10.4276 | 4 | 10.4276 | 40.1726 | 20.0863 | 20 | 20 | 0.086323 | -22.717
1480 | 24.6667 | 1.9954 | 10.3852 | 2 | 10.4 | 40.1762 | 0 | 0.014817 | 127.6782 | -5.6303e-05 | 0.04445 | 6.3839 | -0.00016891 | 6.4282 |  | 10.4282 | 4 | 10.4282 | 40.1762 | 20.0881 | 20 | 20 | 0.0881 | -22.6289
1481 | 24.6833 | 1.9954 | 10.3852 | 2 | 10.4 | 40.1797 | 0 | 0.014759 | 127.693 | -5.7461e-05 | 0.044278 | 6.3846 | -0.00017238 | 6.4288 |  | 10.4288 | 4 | 10.4288 | 40.1797 | 20.0899 | 20 | 20 | 0.089856 | -22.539
1482 | 24.7 | 1.9954 | 10.3853 | 2 | 10.4 | 40.1832 | 0 | 0.014701 | 127.7077 | -5.8607e-05 | 0.044102 | 6.3854 | -0.00017582 | 6.4293 |  | 10.4293 | 4 | 10.4293 | 40.1832 | 20.0916 | 20 | 20 | 0.091593 | -22.4474
1483 | 24.7167 | 1.9954 | 10.3854 | 2 | 10.4 | 40.1866 | 0 | 0.014641 | 127.7223 | -5.974e-05 | 0.043923 | 6.3861 | -0.00017922 | 6.4299 |  | 10.4299 | 4 | 10.4299 | 40.1866 | 20.0933 | 20 | 20 | 0.09331 | -22.3541
1484 | 24.7333 | 1.9954 | 10.3854 | 2 | 10.4 | 40.19 | 0 | 0.01458 | 127.7369 | -6.0859e-05 | 0.04374 | 6.3868 | -0.00018258 | 6.4304 |  | 10.4304 | 4 | 10.4304 | 40.19 | 20.095 | 20 | 20 | 0.095007 | -22.2591
1485 | 24.75 | 1.9955 | 10.3855 | 2 | 10.4 | 40.1934 | 0 | 0.014518 | 127.7514 | -6.1966e-05 | 0.043554 | 6.3876 | -0.0001859 | 6.4309 |  | 10.4309 | 4 | 10.4309 | 40.1934 | 20.0967 | 20 | 20 | 0.096684 | -22.1624
1486 | 24.7667 | 1.9955 | 10.3855 | 2 | 10.4 | 40.1967 | 0 | 0.014455 | 127.7659 | -6.306e-05 | 0.043365 | 6.3883 | -0.00018918 | 6.4315 |  | 10.4315 | 4 | 10.4315 | 40.1967 | 20.0983 | 20 | 20 | 0.098341 | -22.0641
1487 | 24.7833 | 1.9955 | 10.3856 | 2 | 10.4 | 40.2 | 0 | 0.014391 | 127.7803 | -6.4141e-05 | 0.043172 | 6.389 | -0.00019242 | 6.432 |  | 10.432 | 4 | 10.432 | 40.2 | 20.1 | 20 | 20 | 0.099978 | -21.9641
1488 | 24.8 | 1.9955 | 10.3857 | 2 | 10.4 | 40.2032 | 0 | 0.014326 | 127.7946 | -6.5209e-05 | 0.042977 | 6.3897 | -0.00019563 | 6.4325 |  | 10.4325 | 4 | 10.4325 | 40.2032 | 20.1016 | 20 | 20 | 0.1016 | -21.8625
1489 | 24.8167 | 1.9955 | 10.3857 | 2 | 10.4 | 40.2064 | 0 | 0.014259 | 127.8088 | -6.6263e-05 | 0.042778 | 6.3904 | -0.00019879 | 6.433 |  | 10.433 | 4 | 10.433 | 40.2064 | 20.1032 | 20 | 20 | 0.10319 | -21.7593
1490 | 24.8333 | 1.9956 | 10.3858 | 2 | 10.4 | 40.2095 | 0 | 0.014192 | 127.823 | -6.7305e-05 | 0.042576 | 6.3912 | -0.00020192 | 6.4335 |  | 10.4335 | 4 | 10.4335 | 40.2095 | 20.1048 | 20 | 20 | 0.10477 | -21.6545
1491 | 24.85 | 1.9956 | 10.3859 | 2 | 10.4 | 40.2127 | 0 | 0.014124 | 127.8372 | -6.8333e-05 | 0.042371 | 6.3919 | -0.000205 | 6.434 |  | 10.434 | 4 | 10.434 | 40.2127 | 20.1063 | 20 | 20 | 0.10633 | -21.5482
1492 | 24.8667 | 1.9956 | 10.3859 | 2 | 10.4 | 40.2157 | 0 | 0.014054 | 127.8512 | -6.9349e-05 | 0.042163 | 6.3926 | -0.00020805 | 6.4345 |  | 10.4345 | 4 | 10.4345 | 40.2157 | 20.1079 | 20 | 20 | 0.10786 | -21.4403
1493 | 24.8833 | 1.9956 | 10.386 | 2 | 10.4 | 40.2188 | 0 | 0.013984 | 127.8652 | -7.0351e-05 | 0.041952 | 6.3933 | -0.00021105 | 6.435 |  | 10.435 | 4 | 10.435 | 40.2188 | 20.1094 | 20 | 20 | 0.10938 | -21.331
1494 | 24.9 | 1.9957 | 10.3861 | 2 | 10.4 | 40.2217 | 0 | 0.013913 | 127.8791 | -7.134e-05 | 0.041738 | 6.394 | -0.00021402 | 6.4355 |  | 10.4355 | 4 | 10.4355 | 40.2217 | 20.1109 | 20 | 20 | 0.11087 | -21.2201
1495 | 24.9167 | 1.9957 | 10.3862 | 2 | 10.4 | 40.2247 | 0 | 0.01384 | 127.893 | -7.2315e-05 | 0.041521 | 6.3946 | -0.00021695 | 6.436 |  | 10.436 | 4 | 10.436 | 40.2247 | 20.1123 | 20 | 20 | 0.11235 | -21.1077
1496 | 24.9333 | 1.9957 | 10.3862 | 2 | 10.4 | 40.2276 | 0 | 0.013767 | 127.9067 | -7.3277e-05 | 0.041301 | 6.3953 | -0.00021983 | 6.4364 |  | 10.4364 | 4 | 10.4364 | 40.2276 | 20.1138 | 20 | 20 | 0.1138 | -20.9939
1497 | 24.95 | 1.9957 | 10.3863 | 2 | 10.4 | 40.2305 | 0 | 0.013693 | 127.9204 | -7.4227e-05 | 0.041079 | 6.396 | -0.00022268 | 6.4369 |  | 10.4369 | 4 | 10.4369 | 40.2305 | 20.1152 | 20 | 20 | 0.11524 | -20.8787
1498 | 24.9667 | 1.9957 | 10.3864 | 2 | 10.4 | 40.2333 | 0 | 0.013618 | 127.934 | -7.5162e-05 | 0.040853 | 6.3967 | -0.00022549 | 6.4373 |  | 10.4373 | 4 | 10.4373 | 40.2333 | 20.1167 | 20 | 20 | 0.11665 | -20.762
1499 | 24.9833 | 1.9958 | 10.3865 | 2 | 10.4 | 40.2361 | 0 | 0.013542 | 127.9476 | -7.6085e-05 | 0.040625 | 6.3974 | -0.00022825 | 6.4378 |  | 10.4378 | 4 | 10.4378 | 40.2361 | 20.118 | 20 | 20 | 0.11805 | -20.644
1500 | 25 | 1.9958 | 10.3865 | 2 | 10.4 | 40.2388 | 0 | 0.013465 | 127.961 | -7.6994e-05 | 0.040394 | 6.3981 | -0.00023098 | 6.4382 |  | 10.4382 | 4 | 10.4382 | 40.2388 | 20.1194 | 20 | 20 | 0.11942 | -20.5246
1501 | 25.0167 | 1.9958 | 10.3866 | 2 | 10.4 | 40.2415 | 0 | 0.013387 | 127.9744 | -7.789e-05 | 0.04016 | 6.3987 | -0.00023367 | 6.4386 |  | 10.4386 | 4 | 10.4386 | 40.2415 | 20.1208 | 20 | 20 | 0.12077 | -20.4038
1502 | 25.0333 | 1.9958 | 10.3867 | 2 | 10.4 | 40.2442 | 0 | 0.013308 | 127.9877 | -7.8772e-05 | 0.039924 | 6.3994 | -0.00023632 | 6.4391 |  | 10.4391 | 4 | 10.4391 | 40.2442 | 20.1221 | 20 | 20 | 0.12211 | -20.2817
1503 | 25.05 | 1.9959 | 10.3868 | 2 | 10.4 | 40.2468 | 0 | 0.013228 | 128.001 | -7.9641e-05 | 0.039685 | 6.4 | -0.00023892 | 6.4395 |  | 10.4395 | 4 | 10.4395 | 40.2468 | 20.1234 | 20 | 20 | 0.12342 | -20.1583
1504 | 25.0667 | 1.9959 | 10.3869 | 2 | 10.4 | 40.2494 | 0 | 0.013148 | 128.0141 | -8.0497e-05 | 0.039443 | 6.4007 | -0.00024149 | 6.4399 |  | 10.4399 | 4 | 10.4399 | 40.2494 | 20.1247 | 20 | 20 | 0.12471 | -20.0336
1505 | 25.0833 | 1.9959 | 10.3869 | 2 | 10.4 | 40.252 | 0 | 0.013066 | 128.0272 | -8.134e-05 | 0.039199 | 6.4014 | -0.00024402 | 6.4403 |  | 10.4403 | 4 | 10.4403 | 40.252 | 20.126 | 20 | 20 | 0.12598 | -19.9076
1506 | 25.1 | 1.9959 | 10.387 | 2 | 10.4 | 40.2545 | 0 | 0.012984 | 128.0402 | -8.2169e-05 | 0.038953 | 6.402 | -0.00024651 | 6.4407 |  | 10.4407 | 4 | 10.4407 | 40.2545 | 20.1272 | 20 | 20 | 0.12723 | -19.7803
1507 | 25.1167 | 1.996 | 10.3871 | 2 | 10.4 | 40.2569 | 0 | 0.012901 | 128.0531 | -8.2985e-05 | 0.038704 | 6.4027 | -0.00024895 | 6.4411 |  | 10.4411 | 4 | 10.4411 | 40.2569 | 20.1285 | 20 | 20 | 0.12846 | -19.6519
1508 | 25.1333 | 1.996 | 10.3872 | 2 | 10.4 | 40.2593 | 0 | 0.012818 | 128.0659 | -8.3787e-05 | 0.038453 | 6.4033 | -0.00025136 | 6.4415 |  | 10.4415 | 4 | 10.4415 | 40.2593 | 20.1297 | 20 | 20 | 0.12967 | -19.5222
1509 | 25.15 | 1.996 | 10.3873 | 2 | 10.4 | 40.2617 | 0 | 0.012733 | 128.0786 | -8.4576e-05 | 0.038199 | 6.4039 | -0.00025373 | 6.4419 |  | 10.4419 | 4 | 10.4419 | 40.2617 | 20.1309 | 20 | 20 | 0.13086 | -19.3914
1510 | 25.1667 | 1.996 | 10.3874 | 2 | 10.4 | 40.2641 | 0 | 0.012648 | 128.0913 | -8.5352e-05 | 0.037943 | 6.4046 | -0.00025605 | 6.4422 |  | 10.4422 | 4 | 10.4422 | 40.2641 | 20.132 | 20 | 20 | 0.13203 | -19.2593
1511 | 25.1833 | 1.9961 | 10.3874 | 2 | 10.4 | 40.2664 | 0 | 0.012561 | 128.1038 | -8.6114e-05 | 0.037684 | 6.4052 | -0.00025834 | 6.4426 |  | 10.4426 | 4 | 10.4426 | 40.2664 | 20.1332 | 20 | 20 | 0.13318 | -19.1261
1512 | 25.2 | 1.9961 | 10.3875 | 2 | 10.4 | 40.2686 | 0 | 0.012475 | 128.1163 | -8.6863e-05 | 0.037424 | 6.4058 | -0.00026059 | 6.443 |  | 10.443 | 4 | 10.443 | 40.2686 | 20.1343 | 20 | 20 | 0.13431 | -18.9918
1513 | 25.2167 | 1.9961 | 10.3876 | 2 | 10.4 | 40.2708 | 0 | 0.012387 | 128.1287 | -8.7598e-05 | 0.037161 | 6.4064 | -0.0002628 | 6.4433 |  | 10.4433 | 4 | 10.4433 | 40.2708 | 20.1354 | 20 | 20 | 0.13541 | -18.8564
1514 | 25.2333 | 1.9962 | 10.3877 | 2 | 10.4 | 40.273 | 0 | 0.012299 | 128.141 | -8.8321e-05 | 0.036896 | 6.407 | -0.00026496 | 6.4437 |  | 10.4437 | 4 | 10.4437 | 40.273 | 20.1365 | 20 | 20 | 0.1365 | -18.7199
1515 | 25.25 | 1.9962 | 10.3878 | 2 | 10.4 | 40.2751 | 0 | 0.01221 | 128.1532 | -8.903e-05 | 0.036629 | 6.4077 | -0.00026709 | 6.444 |  | 10.444 | 4 | 10.444 | 40.2751 | 20.1376 | 20 | 20 | 0.13757 | -18.5824
1516 | 25.2667 | 1.9962 | 10.3879 | 2 | 10.4 | 40.2772 | 0 | 0.01212 | 128.1653 | -8.9725e-05 | 0.03636 | 6.4083 | -0.00026918 | 6.4444 |  | 10.4444 | 4 | 10.4444 | 40.2772 | 20.1386 | 20 | 20 | 0.13861 | -18.4437
1517 | 25.2833 | 1.9962 | 10.388 | 2 | 10.4 | 40.2793 | 0 | 0.01203 | 128.1773 | -9.0407e-05 | 0.036089 | 6.4089 | -0.00027122 | 6.4447 |  | 10.4447 | 4 | 10.4447 | 40.2793 | 20.1396 | 20 | 20 | 0.13964 | -18.3041
1518 | 25.3 | 1.9963 | 10.3881 | 2 | 10.4 | 40.2813 | 0 | 0.011938 | 128.1893 | -9.1076e-05 | 0.035815 | 6.4095 | -0.00027323 | 6.445 |  | 10.445 | 4 | 10.445 | 40.2813 | 20.1406 | 20 | 20 | 0.14064 | -18.1635
1519 | 25.3167 | 1.9963 | 10.3882 | 2 | 10.4 | 40.2833 | 0 | 0.011847 | 128.2011 | -9.1732e-05 | 0.03554 | 6.4101 | -0.0002752 | 6.4453 |  | 10.4453 | 4 | 10.4453 | 40.2833 | 20.1416 | 20 | 20 | 0.14163 | -18.0218
1520 | 25.3333 | 1.9963 | 10.3882 | 2 | 10.4 | 40.2852 | 0 | 0.011754 | 128.2129 | -9.2374e-05 | 0.035263 | 6.4106 | -0.00027712 | 6.4456 |  | 10.4456 | 4 | 10.4456 | 40.2852 | 20.1426 | 20 | 20 | 0.14259 | -17.8792
1521 | 25.35 | 1.9964 | 10.3883 | 2 | 10.4 | 40.2871 | 0 | 0.011661 | 128.2245 | -9.3004e-05 | 0.034984 | 6.4112 | -0.00027901 | 6.4459 |  | 10.4459 | 4 | 10.4459 | 40.2871 | 20.1435 | 20 | 20 | 0.14354 | -17.7357
1522 | 25.3667 | 1.9964 | 10.3884 | 2 | 10.4 | 40.2889 | 0 | 0.011568 | 128.2361 | -9.3619e-05 | 0.034703 | 6.4118 | -0.00028086 | 6.4462 |  | 10.4462 | 4 | 10.4462 | 40.2889 | 20.1445 | 20 | 20 | 0.14446 | -17.5912
1523 | 25.3833 | 1.9964 | 10.3885 | 2 | 10.4 | 40.2907 | 0 | 0.011474 | 128.2476 | -9.4222e-05 | 0.034421 | 6.4124 | -0.00028267 | 6.4465 |  | 10.4465 | 4 | 10.4465 | 40.2907 | 20.1454 | 20 | 20 | 0.14537 | -17.4459
1524 | 25.4 | 1.9964 | 10.3886 | 2 | 10.4 | 40.2925 | 0 | 0.011379 | 128.259 | -9.4812e-05 | 0.034136 | 6.4129 | -0.00028443 | 6.4468 |  | 10.4468 | 4 | 10.4468 | 40.2925 | 20.1462 | 20 | 20 | 0.14625 | -17.2996
1525 | 25.4167 | 1.9965 | 10.3887 | 2 | 10.4 | 40.2942 | 0 | 0.011283 | 128.2702 | -9.5388e-05 | 0.03385 | 6.4135 | -0.00028616 | 6.4471 |  | 10.4471 | 4 | 10.4471 | 40.2942 | 20.1471 | 20 | 20 | 0.14711 | -17.1525
1526 | 25.4333 | 1.9965 | 10.3888 | 2 | 10.4 | 40.2959 | 0 | 0.011187 | 128.2814 | -9.5951e-05 | 0.033562 | 6.4141 | -0.00028785 | 6.4473 |  | 10.4473 | 4 | 10.4473 | 40.2959 | 20.148 | 20 | 20 | 0.14796 | -17.0046
1527 | 25.45 | 1.9965 | 10.3889 | 2 | 10.4 | 40.2976 | 0 | 0.011091 | 128.2925 | -9.6501e-05 | 0.033273 | 6.4146 | -0.0002895 | 6.4476 |  | 10.4476 | 4 | 10.4476 | 40.2976 | 20.1488 | 20 | 20 | 0.14878 | -16.8558
1528 | 25.4667 | 1.9966 | 10.389 | 2 | 10.4 | 40.2992 | 0 | 0.010994 | 128.3035 | -9.7038e-05 | 0.032982 | 6.4152 | -0.00029111 | 6.4479 |  | 10.4479 | 4 | 10.4479 | 40.2992 | 20.1496 | 20 | 20 | 0.14958 | -16.7062
1529 | 25.4833 | 1.9966 | 10.3891 | 2 | 10.4 | 40.3007 | 0 | 0.010896 | 128.3144 | -9.7562e-05 | 0.032689 | 6.4157 | -0.00029268 | 6.4481 |  | 10.4481 | 4 | 10.4481 | 40.3007 | 20.1504 | 20 | 20 | 0.15036 | -16.5558
1530 | 25.5 | 1.9966 | 10.3892 | 2 | 10.4 | 40.3023 | 0 | 0.010798 | 128.3252 | -9.8072e-05 | 0.032395 | 6.4163 | -0.00029422 | 6.4484 |  | 10.4484 | 4 | 10.4484 | 40.3023 | 20.1511 | 20 | 20 | 0.15113 | -16.4047
1531 | 25.5167 | 1.9967 | 10.3893 | 2 | 10.4 | 40.3037 | 0 | 0.0107 | 128.3359 | -9.857e-05 | 0.032099 | 6.4168 | -0.00029571 | 6.4486 |  | 10.4486 | 4 | 10.4486 | 40.3037 | 20.1519 | 20 | 20 | 0.15187 | -16.2528
1532 | 25.5333 | 1.9967 | 10.3894 | 2 | 10.4 | 40.3052 | 0 | 0.010601 | 128.3465 | -9.9055e-05 | 0.031802 | 6.4173 | -0.00029716 | 6.4488 |  | 10.4488 | 4 | 10.4488 | 40.3052 | 20.1526 | 20 | 20 | 0.15259 | -16.1002
1533 | 25.55 | 1.9967 | 10.3895 | 2 | 10.4 | 40.3066 | 0 | 0.010501 | 128.357 | -9.9526e-05 | 0.031503 | 6.4179 | -0.00029858 | 6.4491 |  | 10.4491 | 4 | 10.4491 | 40.3066 | 20.1533 | 20 | 20 | 0.1533 | -15.9469
1534 | 25.5667 | 1.9967 | 10.3896 | 2 | 10.4 | 40.308 | 0 | 0.010401 | 128.3674 | -9.9985e-05 | 0.031203 | 6.4184 | -0.00029995 | 6.4493 |  | 10.4493 | 4 | 10.4493 | 40.308 | 20.154 | 20 | 20 | 0.15398 | -15.793
1535 | 25.5833 | 1.9968 | 10.3897 | 2 | 10.4 | 40.3093 | 0 | 0.010301 | 128.3777 | -0.00010043 | 0.030902 | 6.4189 | -0.00030129 | 6.4495 |  | 10.4495 | 4 | 10.4495 | 40.3093 | 20.1546 | 20 | 20 | 0.15464 | -15.6383
1536 | 25.6 | 1.9968 | 10.3898 | 2 | 10.4 | 40.3106 | 0 | 0.0102 | 128.3879 | -0.00010086 | 0.030599 | 6.4194 | -0.00030259 | 6.4497 |  | 10.4497 | 4 | 10.4497 | 40.3106 | 20.1553 | 20 | 20 | 0.15529 | -15.483
1537 | 25.6167 | 1.9968 | 10.3899 | 2 | 10.4 | 40.3118 | 0 | 0.010098 | 128.398 | -0.00010128 | 0.030295 | 6.4199 | -0.00030385 | 6.4499 |  | 10.4499 | 4 | 10.4499 | 40.3118 | 20.1559 | 20 | 20 | 0.15591 | -15.3271
1538 | 25.6333 | 1.9969 | 10.39 | 2 | 10.4 | 40.313 | 0 | 0.0099968 | 128.408 | -0.00010169 | 0.02999 | 6.4204 | -0.00030507 | 6.4501 |  | 10.4501 | 4 | 10.4501 | 40.313 | 20.1565 | 20 | 20 | 0.15652 | -15.1706
1539 | 25.65 | 1.9969 | 10.3901 | 2 | 10.4 | 40.3142 | 0 | 0.0098947 | 128.4179 | -0.00010209 | 0.029684 | 6.4209 | -0.00030626 | 6.4503 |  | 10.4503 | 4 | 10.4503 | 40.3142 | 20.1571 | 20 | 20 | 0.1571 | -15.0135
1540 | 25.6667 | 1.9969 | 10.3902 | 2 | 10.4 | 40.3153 | 0 | 0.0097922 | 128.4277 | -0.00010247 | 0.029377 | 6.4214 | -0.0003074 | 6.4505 |  | 10.4505 | 4 | 10.4505 | 40.3153 | 20.1577 | 20 | 20 | 0.15767 | -14.8558
1541 | 25.6833 | 1.997 | 10.3903 | 2 | 10.4 | 40.3164 | 0 | 0.0096894 | 128.4374 | -0.00010284 | 0.029068 | 6.4219 | -0.00030851 | 6.4506 |  | 10.4506 | 4 | 10.4506 | 40.3164 | 20.1582 | 20 | 20 | 0.15822 | -14.6976
1542 | 25.7 | 1.997 | 10.3904 | 2 | 10.4 | 40.3175 | 0 | 0.0095862 | 128.447 | -0.00010319 | 0.028759 | 6.4223 | -0.00030958 | 6.4508 |  | 10.4508 | 4 | 10.4508 | 40.3175 | 20.1587 | 20 | 20 | 0.15874 | -14.5389
1543 | 25.7167 | 1.997 | 10.3905 | 2 | 10.4 | 40.3185 | 0 | 0.0094827 | 128.4565 | -0.00010354 | 0.028448 | 6.4228 | -0.00031061 | 6.451 |  | 10.451 | 4 | 10.451 | 40.3185 | 20.1593 | 20 | 20 | 0.15925 | -14.3796
1544 | 25.7333 | 1.9971 | 10.3906 | 2 | 10.4 | 40.3195 | 0 | 0.0093788 | 128.4658 | -0.00010387 | 0.028136 | 6.4233 | -0.0003116 | 6.4511 |  | 10.4511 | 4 | 10.4511 | 40.3195 | 20.1597 | 20 | 20 | 0.15974 | -14.2199
1545 | 25.75 | 1.9971 | 10.3907 | 2 | 10.4 | 40.3204 | 0 | 0.0092746 | 128.4751 | -0.00010419 | 0.027824 | 6.4238 | -0.00031256 | 6.4513 |  | 10.4513 | 4 | 10.4513 | 40.3204 | 20.1602 | 20 | 20 | 0.16021 | -14.0597
1546 | 25.7667 | 1.9971 | 10.3908 | 2 | 10.4 | 40.3213 | 0 | 0.0091701 | 128.4843 | -0.00010449 | 0.02751 | 6.4242 | -0.00031348 | 6.4514 |  | 10.4514 | 4 | 10.4514 | 40.3213 | 20.1607 | 20 | 20 | 0.16066 | -13.899
1547 | 25.7833 | 1.9972 | 10.3909 | 2 | 10.4 | 40.3222 | 0 | 0.0090653 | 128.4933 | -0.00010479 | 0.027196 | 6.4247 | -0.00031436 | 6.4515 |  | 10.4515 | 4 | 10.4515 | 40.3222 | 20.1611 | 20 | 20 | 0.16109 | -13.7379
1548 | 25.8 | 1.9972 | 10.391 | 2 | 10.4 | 40.323 | 0 | 0.0089603 | 128.5023 | -0.00010507 | 0.026881 | 6.4251 | -0.0003152 | 6.4517 |  | 10.4517 | 4 | 10.4517 | 40.323 | 20.1615 | 20 | 20 | 0.1615 | -13.5764
1549 | 25.8167 | 1.9972 | 10.3911 | 2 | 10.4 | 40.3238 | 0 | 0.0088549 | 128.5112 | -0.00010534 | 0.026565 | 6.4256 | -0.00031601 | 6.4518 |  | 10.4518 | 4 | 10.4518 | 40.3238 | 20.1619 | 20 | 20 | 0.1619 | -13.4145
1550 | 25.8333 | 1.9973 | 10.3913 | 2 | 10.4 | 40.3245 | 0 | 0.0087493 | 128.5199 | -0.00010559 | 0.026248 | 6.426 | -0.00031678 | 6.4519 |  | 10.4519 | 4 | 10.4519 | 40.3245 | 20.1623 | 20 | 20 | 0.16227 | -13.2523
1551 | 25.85 | 1.9973 | 10.3914 | 2 | 10.4 | 40.3253 | 0 | 0.0086435 | 128.5285 | -0.00010584 | 0.025931 | 6.4264 | -0.00031751 | 6.452 |  | 10.452 | 4 | 10.452 | 40.3253 | 20.1626 | 20 | 20 | 0.16263 | -13.0896
1552 | 25.8667 | 1.9973 | 10.3915 | 2 | 10.4 | 40.3259 | 0 | 0.0085374 | 128.5371 | -0.00010607 | 0.025612 | 6.4269 | -0.00031821 | 6.4521 |  | 10.4521 | 4 | 10.4521 | 40.3259 | 20.163 | 20 | 20 | 0.16296 | -12.9267
1553 | 25.8833 | 1.9974 | 10.3916 | 2 | 10.4 | 40.3266 | 0 | 0.0084312 | 128.5455 | -0.00010629 | 0.025293 | 6.4273 | -0.00031887 | 6.4523 |  | 10.4523 | 4 | 10.4523 | 40.3266 | 20.1633 | 20 | 20 | 0.16328 | -12.7634
1554 | 25.9 | 1.9974 | 10.3917 | 2 | 10.4 | 40.3272 | 0 | 0.0083247 | 128.5538 | -0.0001065 | 0.024974 | 6.4277 | -0.00031949 | 6.4523 |  | 10.4523 | 4 | 10.4523 | 40.3272 | 20.1636 | 20 | 20 | 0.16358 | -12.5998
1555 | 25.9167 | 1.9974 | 10.3918 | 2 | 10.4 | 40.3277 | 0 | 0.008218 | 128.5621 | -0.00010669 | 0.024654 | 6.4281 | -0.00032008 | 6.4524 |  | 10.4524 | 4 | 10.4524 | 40.3277 | 20.1639 | 20 | 20 | 0.16387 | -12.4359
1556 | 25.9333 | 1.9975 | 10.3919 | 2 | 10.4 | 40.3283 | 0 | 0.0081111 | 128.5702 | -0.00010688 | 0.024333 | 6.4285 | -0.00032063 | 6.4525 |  | 10.4525 | 4 | 10.4525 | 40.3283 | 20.1641 | 20 | 20 | 0.16413 | -12.2718
1557 | 25.95 | 1.9975 | 10.392 | 2 | 10.4 | 40.3287 | 0 | 0.008004 | 128.5782 | -0.00010705 | 0.024012 | 6.4289 | -0.00032115 | 6.4526 |  | 10.4526 | 4 | 10.4526 | 40.3287 | 20.1644 | 20 | 20 | 0.16437 | -12.1074
1558 | 25.9667 | 1.9975 | 10.3921 | 2 | 10.4 | 40.3292 | 0 | 0.0078968 | 128.5861 | -0.00010721 | 0.02369 | 6.4293 | -0.00032163 | 6.4527 |  | 10.4527 | 4 | 10.4527 | 40.3292 | 20.1646 | 20 | 20 | 0.1646 | -11.9428
1559 | 25.9833 | 1.9976 | 10.3922 | 2 | 10.4 | 40.3296 | 0 | 0.0077895 | 128.5939 | -0.00010736 | 0.023368 | 6.4297 | -0.00032207 | 6.4527 |  | 10.4527 | 4 | 10.4527 | 40.3296 | 20.1648 | 20 | 20 | 0.16481 | -11.778
1560 | 26 | 1.9976 | 10.3923 | 2 | 10.4 | 40.33 | 0 | 0.007682 | 128.6015 | -0.00010749 | 0.023046 | 6.4301 | -0.00032248 | 6.4528 |  | 10.4528 | 4 | 10.4528 | 40.33 | 20.165 | 20 | 20 | 0.165 | -11.613
1561 | 26.0167 | 1.9976 | 10.3924 | 2 | 10.4 | 40.3304 | 0 | 0.0075744 | 128.6091 | -0.00010762 | 0.022723 | 6.4305 | -0.00032286 | 6.4529 |  | 10.4529 | 4 | 10.4529 | 40.3304 | 20.1652 | 20 | 20 | 0.16518 | -11.4478
1562 | 26.0333 | 1.9977 | 10.3925 | 2 | 10.4 | 40.3307 | 0 | 0.0074666 | 128.6166 | -0.00010773 | 0.0224 | 6.4308 | -0.0003232 | 6.4529 |  | 10.4529 | 4 | 10.4529 | 40.3307 | 20.1653 | 20 | 20 | 0.16533 | -11.2825
1563 | 26.05 | 1.9977 | 10.3926 | 2 | 10.4 | 40.3309 | 0 | 0.0073588 | 128.6239 | -0.00010783 | 0.022076 | 6.4312 | -0.0003235 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3309 | 20.1655 | 20 | 20 | 0.16547 | -11.117
1564 | 26.0667 | 1.9977 | 10.3927 | 2 | 10.4 | 40.3312 | 0 | 0.0072509 | 128.6312 | -0.00010792 | 0.021753 | 6.4316 | -0.00032377 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3312 | 20.1656 | 20 | 20 | 0.16559 | -10.9515
1565 | 26.0833 | 1.9978 | 10.3929 | 2 | 10.4 | 40.3314 | 0 | 0.0071429 | 128.6383 | -0.000108 | 0.021429 | 6.4319 | -0.00032401 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3314 | 20.1657 | 20 | 20 | 0.16569 | -10.7858
1566 | 26.1 | 1.9978 | 10.393 | 2 | 10.4 | 40.3316 | 0 | 0.0070348 | 128.6454 | -0.00010807 | 0.021104 | 6.4323 | -0.00032421 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3316 | 20.1658 | 20 | 20 | 0.16578 | -10.62
1567 | 26.1167 | 1.9978 | 10.3931 | 2 | 10.4 | 40.3317 | 0 | 0.0069267 | 128.6523 | -0.00010812 | 0.02078 | 6.4326 | -0.00032437 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3317 | 20.1658 | 20 | 20 | 0.16585 | -10.4541
1568 | 26.1333 | 1.9979 | 10.3932 | 2 | 10.4 | 40.3318 | 0 | 0.0068185 | 128.6591 | -0.00010817 | 0.020455 | 6.433 | -0.00032451 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3318 | 20.1659 | 20 | 20 | 0.1659 | -10.2882
1569 | 26.15 | 1.9979 | 10.3933 | 2 | 10.4 | 40.3319 | 0 | 0.0067103 | 128.6658 | -0.0001082 | 0.020131 | 6.4333 | -0.00032461 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3319 | 20.1659 | 20 | 20 | 0.16593 | -10.1223
1570 | 26.1667 | 1.9979 | 10.3934 | 2 | 10.4 | 40.3319 | 0 | 0.0066021 | 128.6724 | -0.00010822 | 0.019806 | 6.4336 | -0.00032467 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3319 | 20.1659 | 20 | 20 | 0.16595 | -9.9564
1571 | 26.1833 | 1.998 | 10.3935 | 2 | 10.4 | 40.3319 | 0 | 0.0064938 | 128.6789 | -0.00010824 | 0.019482 | 6.4339 | -0.00032471 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3319 | 20.1659 | 20 | 20 | 0.16595 | -9.7904
1572 | 26.2 | 1.998 | 10.3936 | 2 | 10.4 | 40.3319 | 0 | 0.0063856 | 128.6853 | -0.00010824 | 0.019157 | 6.4343 | -0.00032471 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3319 | 20.1659 | 20 | 20 | 0.16593 | -9.6245
1573 | 26.2167 | 1.998 | 10.3937 | 2 | 10.4 | 40.3318 | 0 | 0.0062774 | 128.6916 | -0.00010822 | 0.018832 | 6.4346 | -0.00032467 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3318 | 20.1659 | 20 | 20 | 0.1659 | -9.4586
1574 | 26.2333 | 1.9981 | 10.3938 | 2 | 10.4 | 40.3317 | 0 | 0.0061692 | 128.6978 | -0.0001082 | 0.018508 | 6.4349 | -0.00032461 | 6.4531 |  | 10.4531 | 4 | 10.4531 | 40.3317 | 20.1658 | 20 | 20 | 0.16585 | -9.2927
1575 | 26.25 | 1.9981 | 10.3939 | 2 | 10.4 | 40.3316 | 0 | 0.006061 | 128.7038 | -0.00010817 | 0.018183 | 6.4352 | -0.00032451 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3316 | 20.1658 | 20 | 20 | 0.16578 | -9.127
1576 | 26.2667 | 1.9981 | 10.394 | 2 | 10.4 | 40.3314 | 0 | 0.0059529 | 128.7098 | -0.00010813 | 0.017859 | 6.4355 | -0.00032438 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3314 | 20.1657 | 20 | 20 | 0.1657 | -8.9613
1577 | 26.2833 | 1.9982 | 10.3942 | 2 | 10.4 | 40.3312 | 0 | 0.0058448 | 128.7156 | -0.00010807 | 0.017534 | 6.4358 | -0.00032422 | 6.453 |  | 10.453 | 4 | 10.453 | 40.3312 | 20.1656 | 20 | 20 | 0.1656 | -8.7957
1578 | 26.3 | 1.9982 | 10.3943 | 2 | 10.4 | 40.331 | 0 | 0.0057368 | 128.7214 | -0.00010801 | 0.01721 | 6.4361 | -0.00032402 | 6.453 |  | 10.453 | 4 | 10.453 | 40.331 | 20.1655 | 20 | 20 | 0.16548 | -8.6302
1579 | 26.3167 | 1.9982 | 10.3944 | 2 | 10.4 | 40.3307 | 0 | 0.0056289 | 128.727 | -0.00010793 | 0.016887 | 6.4363 | -0.00032379 | 6.4529 |  | 10.4529 | 4 | 10.4529 | 40.3307 | 20.1653 | 20 | 20 | 0.16535 | -8.4648
1580 | 26.3333 | 1.9983 | 10.3945 | 2 | 10.4 | 40.3304 | 0 | 0.005521 | 128.7325 | -0.00010785 | 0.016563 | 6.4366 | -0.00032354 | 6.4529 |  | 10.4529 | 4 | 10.4529 | 40.3304 | 20.1652 | 20 | 20 | 0.1652 | -8.2996
1581 | 26.35 | 1.9983 | 10.3946 | 2 | 10.4 | 40.3301 | 0 | 0.0054133 | 128.7379 | -0.00010775 | 0.01624 | 6.4369 | -0.00032325 | 6.4528 |  | 10.4528 | 4 | 10.4528 | 40.3301 | 20.165 | 20 | 20 | 0.16504 | -8.1346
1582 | 26.3667 | 1.9983 | 10.3947 | 2 | 10.4 | 40.3297 | 0 | 0.0053056 | 128.7432 | -0.00010764 | 0.015917 | 6.4372 | -0.00032293 | 6.4528 |  | 10.4528 | 4 | 10.4528 | 40.3297 | 20.1649 | 20 | 20 | 0.16486 | -7.9697
1583 | 26.3833 | 1.9984 | 10.3948 | 2 | 10.4 | 40.3293 | 0 | 0.0051981 | 128.7484 | -0.00010753 | 0.015594 | 6.4374 | -0.00032258 | 6.4527 |  | 10.4527 | 4 | 10.4527 | 40.3293 | 20.1647 | 20 | 20 | 0.16466 | -7.8051
1584 | 26.4 | 1.9984 | 10.3949 | 2 | 10.4 | 40.3289 | 0 | 0.0050907 | 128.7535 | -0.0001074 | 0.015272 | 6.4377 | -0.0003222 | 6.4526 |  | 10.4526 | 4 | 10.4526 | 40.3289 | 20.1645 | 20 | 20 | 0.16445 | -7.6406
1585 | 26.4167 | 1.9984 | 10.395 | 2 | 10.4 | 40.3285 | 0 | 0.0049834 | 128.7585 | -0.00010726 | 0.01495 | 6.4379 | -0.00032179 | 6.4526 |  | 10.4526 | 4 | 10.4526 | 40.3285 | 20.1642 | 20 | 20 | 0.16423 | -7.4764
1586 | 26.4333 | 1.9985 | 10.3951 | 2 | 10.4 | 40.328 | 0 | 0.0048763 | 128.7634 | -0.00010711 | 0.014629 | 6.4382 | -0.00032134 | 6.4525 |  | 10.4525 | 4 | 10.4525 | 40.328 | 20.164 | 20 | 20 | 0.16399 | -7.3124
1587 | 26.45 | 1.9985 | 10.3952 | 2 | 10.4 | 40.3275 | 0 | 0.0047694 | 128.7681 | -0.00010696 | 0.014308 | 6.4384 | -0.00032087 | 6.4524 |  | 10.4524 | 4 | 10.4524 | 40.3275 | 20.1637 | 20 | 20 | 0.16373 | -7.1487
1588 | 26.4667 | 1.9985 | 10.3953 | 2 | 10.4 | 40.3269 | 0 | 0.0046626 | 128.7728 | -0.00010679 | 0.013988 | 6.4386 | -0.00032037 | 6.4523 |  | 10.4523 | 4 | 10.4523 | 40.3269 | 20.1635 | 20 | 20 | 0.16346 | -6.9852
1589 | 26.4833 | 1.9986 | 10.3954 | 2 | 10.4 | 40.3263 | 0 | 0.004556 | 128.7774 | -0.00010661 | 0.013668 | 6.4389 | -0.00031984 | 6.4522 |  | 10.4522 | 4 | 10.4522 | 40.3263 | 20.1632 | 20 | 20 | 0.16317 | -6.822
1590 | 26.5 | 1.9986 | 10.3956 | 2 | 10.4 | 40.3257 | 0 | 0.0044495 | 128.7818 | -0.00010643 | 0.013349 | 6.4391 | -0.00031928 | 6.4521 |  | 10.4521 | 4 | 10.4521 | 40.3257 | 20.1629 | 20 | 20 | 0.16287 | -6.6592
1591 | 26.5167 | 1.9986 | 10.3957 | 2 | 10.4 | 40.3251 | 0 | 0.0043433 | 128.7861 | -0.00010623 | 0.01303 | 6.4393 | -0.00031869 | 6.452 |  | 10.452 | 4 | 10.452 | 40.3251 | 20.1626 | 20 | 20 | 0.16256 | -6.4966
1592 | 26.5333 | 1.9987 | 10.3958 | 2 | 10.4 | 40.3245 | 0 | 0.0042373 | 128.7904 | -0.00010603 | 0.012712 | 6.4395 | -0.00031808 | 6.4519 |  | 10.4519 | 4 | 10.4519 | 40.3245 | 20.1622 | 20 | 20 | 0.16223 | -6.3344
1593 | 26.55 | 1.9987 | 10.3959 | 2 | 10.4 | 40.3238 | 0 | 0.0041315 | 128.7945 | -0.00010581 | 0.012394 | 6.4397 | -0.00031743 | 6.4518 |  | 10.4518 | 4 | 10.4518 | 40.3238 | 20.1619 | 20 | 20 | 0.16188 | -6.1725
1594 | 26.5667 | 1.9987 | 10.396 | 2 | 10.4 | 40.3231 | 0 | 0.0040259 | 128.7985 | -0.00010559 | 0.012078 | 6.4399 | -0.00031676 | 6.4517 |  | 10.4517 | 4 | 10.4517 | 40.3231 | 20.1615 | 20 | 20 | 0.16153 | -6.011
1595 | 26.5833 | 1.9988 | 10.3961 | 2 | 10.4 | 40.3223 | 0 | 0.0039205 | 128.8025 | -0.00010535 | 0.011762 | 6.4401 | -0.00031605 | 6.4516 |  | 10.4516 | 4 | 10.4516 | 40.3223 | 20.1612 | 20 | 20 | 0.16115 | -5.8498
1596 | 26.6 | 1.9988 | 10.3962 | 2 | 10.4 | 40.3215 | 0 | 0.0038154 | 128.8063 | -0.00010511 | 0.011446 | 6.4403 | -0.00031532 | 6.4514 |  | 10.4514 | 4 | 10.4514 | 40.3215 | 20.1608 | 20 | 20 | 0.16077 | -5.6891
1597 | 26.6167 | 1.9988 | 10.3963 | 2 | 10.4 | 40.3207 | 0 | 0.0037106 | 128.81 | -0.00010486 | 0.011132 | 6.4405 | -0.00031457 | 6.4513 |  | 10.4513 | 4 | 10.4513 | 40.3207 | 20.1604 | 20 | 20 | 0.16036 | -5.5287
1598 | 26.6333 | 1.9989 | 10.3964 | 2 | 10.4 | 40.3199 | 0 | 0.003606 | 128.8136 | -0.00010459 | 0.010818 | 6.4407 | -0.00031378 | 6.4512 |  | 10.4512 | 4 | 10.4512 | 40.3199 | 20.1599 | 20 | 20 | 0.15995 | -5.3687
1599 | 26.65 | 1.9989 | 10.3965 | 2 | 10.4 | 40.319 | 0 | 0.0035017 | 128.8171 | -0.00010432 | 0.010505 | 6.4409 | -0.00031297 | 6.451 |  | 10.451 | 4 | 10.451 | 40.319 | 20.1595 | 20 | 20 | 0.15952 | -5.2092
1600 | 26.6667 | 1.9989 | 10.3966 | 2 | 10.4 | 40.3182 | 0 | 0.0033976 | 128.8205 | -0.00010404 | 0.010193 | 6.441 | -0.00031213 | 6.4509 |  | 10.4509 | 4 | 10.4509 | 40.3182 | 20.1591 | 20 | 20 | 0.15908 | -5.0501
1601 | 26.6833 | 1.999 | 10.3967 | 2 | 10.4 | 40.3172 | 0 | 0.0032938 | 128.8238 | -0.00010376 | 0.0098815 | 6.4412 | -0.00031127 | 6.4508 |  | 10.4508 | 4 | 10.4508 | 40.3172 | 20.1586 | 20 | 20 | 0.15862 | -4.8915
1602 | 26.7 | 1.999 | 10.3968 | 2 | 10.4 | 40.3163 | 0 | 0.0031904 | 128.827 | -0.00010346 | 0.0095712 | 6.4413 | -0.00031038 | 6.4506 |  | 10.4506 | 4 | 10.4506 | 40.3163 | 20.1582 | 20 | 20 | 0.15816 | -4.7334
1603 | 26.7167 | 1.999 | 10.3969 | 2 | 10.4 | 40.3153 | 0 | 0.0030872 | 128.8301 | -0.00010315 | 0.0092617 | 6.4415 | -0.00030946 | 6.4505 |  | 10.4505 | 4 | 10.4505 | 40.3153 | 20.1577 | 20 | 20 | 0.15767 | -4.5757
1604 | 26.7333 | 1.9991 | 10.397 | 2 | 10.4 | 40.3144 | 0 | 0.0029844 | 128.8331 | -0.00010284 | 0.0089532 | 6.4417 | -0.00030852 | 6.4503 |  | 10.4503 | 4 | 10.4503 | 40.3144 | 20.1572 | 20 | 20 | 0.15718 | -4.4185
1605 | 26.75 | 1.9991 | 10.3971 | 2 | 10.4 | 40.3133 | 0 | 0.0028819 | 128.8359 | -0.00010252 | 0.0086456 | 6.4418 | -0.00030755 | 6.4501 |  | 10.4501 | 4 | 10.4501 | 40.3133 | 20.1567 | 20 | 20 | 0.15667 | -4.2618
1606 | 26.7667 | 1.9991 | 10.3972 | 2 | 10.4 | 40.3123 | 0 | 0.0027797 | 128.8387 | -0.00010219 | 0.0083391 | 6.4419 | -0.00030656 | 6.45 |  | 10.45 | 4 | 10.45 | 40.3123 | 20.1562 | 20 | 20 | 0.15615 | -4.1057
1607 | 26.7833 | 1.9992 | 10.3973 | 2 | 10.4 | 40.3112 | 0 | 0.0026778 | 128.8414 | -0.00010185 | 0.0080335 | 6.4421 | -0.00030554 | 6.4498 |  | 10.4498 | 4 | 10.4498 | 40.3112 | 20.1556 | 20 | 20 | 0.15562 | -3.9501
1608 | 26.8 | 1.9992 | 10.3974 | 2 | 10.4 | 40.3101 | 0 | 0.0025764 | 128.844 | -0.0001015 | 0.0077291 | 6.4422 | -0.00030449 | 6.4496 |  | 10.4496 | 4 | 10.4496 | 40.3101 | 20.1551 | 20 | 20 | 0.15507 | -3.795
1609 | 26.8167 | 1.9992 | 10.3975 | 2 | 10.4 | 40.309 | 0 | 0.0024752 | 128.8464 | -0.00010114 | 0.0074256 | 6.4423 | -0.00030343 | 6.4494 |  | 10.4494 | 4 | 10.4494 | 40.309 | 20.1545 | 20 | 20 | 0.15451 | -3.6405
1610 | 26.8333 | 1.9993 | 10.3976 | 2 | 10.4 | 40.3079 | 0 | 0.0023744 | 128.8488 | -0.00010078 | 0.0071233 | 6.4424 | -0.00030233 | 6.4493 |  | 10.4493 | 4 | 10.4493 | 40.3079 | 20.1539 | 20 | 20 | 0.15394 | -3.4865
1611 | 26.85 | 1.9993 | 10.3977 | 2 | 10.4 | 40.3067 | 0 | 0.002274 | 128.8511 | -0.00010041 | 0.0068221 | 6.4426 | -0.00030122 | 6.4491 |  | 10.4491 | 4 | 10.4491 | 40.3067 | 20.1534 | 20 | 20 | 0.15336 | -3.3332
1612 | 26.8667 | 1.9993 | 10.3978 | 2 | 10.4 | 40.3055 | 0 | 0.002174 | 128.8533 | -0.00010003 | 0.006522 | 6.4427 | -0.00030008 | 6.4489 |  | 10.4489 | 4 | 10.4489 | 40.3055 | 20.1528 | 20 | 20 | 0.15277 | -3.1804
1613 | 26.8833 | 1.9994 | 10.3979 | 2 | 10.4 | 40.3043 | 0 | 0.0020744 | 128.8553 | -9.9639e-05 | 0.0062231 | 6.4428 | -0.00029892 | 6.4487 |  | 10.4487 | 4 | 10.4487 | 40.3043 | 20.1522 | 20 | 20 | 0.15216 | -3.0283
1614 | 26.9 | 1.9994 | 10.398 | 2 | 10.4 | 40.3031 | 0 | 0.0019751 | 128.8573 | -9.9243e-05 | 0.0059253 | 6.4429 | -0.00029773 | 6.4485 |  | 10.4485 | 4 | 10.4485 | 40.3031 | 20.1515 | 20 | 20 | 0.15154 | -2.8767
1615 | 26.9167 | 1.9994 | 10.3981 | 2 | 10.4 | 40.3018 | 0 | 0.0018763 | 128.8592 | -9.884e-05 | 0.0056288 | 6.443 | -0.00029652 | 6.4483 |  | 10.4483 | 4 | 10.4483 | 40.3018 | 20.1509 | 20 | 20 | 0.15091 | -2.7258
1616 | 26.9333 | 1.9994 | 10.3982 | 2 | 10.4 | 40.3005 | 0 | 0.0017778 | 128.861 | -9.8429e-05 | 0.0053335 | 6.443 | -0.00029529 | 6.4481 |  | 10.4481 | 4 | 10.4481 | 40.3005 | 20.1503 | 20 | 20 | 0.15027 | -2.5755
1617 | 26.95 | 1.9995 | 10.3983 | 2 | 10.4 | 40.2992 | 0 | 0.0016798 | 128.8626 | -9.8011e-05 | 0.0050395 | 6.4431 | -0.00029403 | 6.4479 |  | 10.4479 | 4 | 10.4479 | 40.2992 | 20.1496 | 20 | 20 | 0.14962 | -2.4259
1618 | 26.9667 | 1.9995 | 10.3984 | 2 | 10.4 | 40.2979 | 0 | 0.0015823 | 128.8642 | -9.7586e-05 | 0.0047468 | 6.4432 | -0.00029276 | 6.4477 |  | 10.4477 | 4 | 10.4477 | 40.2979 | 20.149 | 20 | 20 | 0.14895 | -2.277
1619 | 26.9833 | 1.9995 | 10.3985 | 2 | 10.4 | 40.2966 | 0 | 0.0014851 | 128.8657 | -9.7153e-05 | 0.0044553 | 6.4433 | -0.00029146 | 6.4474 |  | 10.4474 | 4 | 10.4474 | 40.2966 | 20.1483 | 20 | 20 | 0.14828 | -2.1287
1620 | 27 | 1.9996 | 10.3986 | 2 | 10.4 | 40.2952 | 0 | 0.0013884 | 128.8671 | -9.6713e-05 | 0.0041652 | 6.4434 | -0.00029014 | 6.4472 |  | 10.4472 | 4 | 10.4472 | 40.2952 | 20.1476 | 20 | 20 | 0.14759 | -1.9811
1621 | 27.0167 | 1.9996 | 10.3987 | 2 | 10.4 | 40.2938 | 0 | 0.0012921 | 128.8684 | -9.6265e-05 | 0.0038764 | 6.4434 | -0.0002888 | 6.447 |  | 10.447 | 4 | 10.447 | 40.2938 | 20.1469 | 20 | 20 | 0.1469 | -1.8342
1622 | 27.0333 | 1.9996 | 10.3988 | 2 | 10.4 | 40.2924 | 0 | 0.0011963 | 128.8696 | -9.5811e-05 | 0.0035889 | 6.4435 | -0.00028743 | 6.4468 |  | 10.4468 | 4 | 10.4468 | 40.2924 | 20.1462 | 20 | 20 | 0.14619 | -1.688
1623 | 27.05 | 1.9997 | 10.3989 | 2 | 10.4 | 40.2909 | 0 | 0.001101 | 128.8707 | -9.535e-05 | 0.0033029 | 6.4435 | -0.00028605 | 6.4466 |  | 10.4466 | 4 | 10.4466 | 40.2909 | 20.1455 | 20 | 20 | 0.14547 | -1.5425
1624 | 27.0667 | 1.9997 | 10.399 | 2 | 10.4 | 40.2895 | 0 | 0.0010061 | 128.8717 | -9.4882e-05 | 0.0030182 | 6.4436 | -0.00028465 | 6.4463 |  | 10.4463 | 4 | 10.4463 | 40.2895 | 20.1447 | 20 | 20 | 0.14475 | -1.3978
1625 | 27.0833 | 1.9997 | 10.3991 | 2 | 10.4 | 40.288 | 0 | 0.00091167 | 128.8726 | -9.4407e-05 | 0.002735 | 6.4436 | -0.00028322 | 6.4461 |  | 10.4461 | 4 | 10.4461 | 40.288 | 20.144 | 20 | 20 | 0.14401 | -1.2538
1626 | 27.1 | 1.9997 | 10.3992 | 2 | 10.4 | 40.2865 | 0 | 0.00081774 | 128.8734 | -9.3926e-05 | 0.0024532 | 6.4437 | -0.00028178 | 6.4458 |  | 10.4458 | 4 | 10.4458 | 40.2865 | 20.1433 | 20 | 20 | 0.14326 | -1.1105
1627 | 27.1167 | 1.9998 | 10.3993 | 2 | 10.4 | 40.285 | 0 | 0.00072431 | 128.8742 | -9.3438e-05 | 0.0021729 | 6.4437 | -0.00028031 | 6.4456 |  | 10.4456 | 4 | 10.4456 | 40.285 | 20.1425 | 20 | 20 | 0.1425 | -0.96801
1628 | 27.1333 | 1.9998 | 10.3994 | 2 | 10.4 | 40.2835 | 0 | 0.00063136 | 128.8748 | -9.2943e-05 | 0.0018941 | 6.4437 | -0.00027883 | 6.4454 |  | 10.4454 | 4 | 10.4454 | 40.2835 | 20.1417 | 20 | 20 | 0.14173 | -0.82627
1629 | 27.15 | 1.9998 | 10.3995 | 2 | 10.4 | 40.2819 | 0 | 0.00053892 | 128.8753 | -9.2442e-05 | 0.0016168 | 6.4438 | -0.00027733 | 6.4451 |  | 10.4451 | 4 | 10.4451 | 40.2819 | 20.141 | 20 | 20 | 0.14096 | -0.68532
1630 | 27.1667 | 1.9999 | 10.3996 | 2 | 10.4 | 40.2803 | 0 | 0.00044699 | 128.8758 | -9.1935e-05 | 0.001341 | 6.4438 | -0.00027581 | 6.4449 |  | 10.4449 | 4 | 10.4449 | 40.2803 | 20.1402 | 20 | 20 | 0.14017 | -0.54515
1631 | 27.1833 | 1.9999 | 10.3996 | 2 | 10.4 | 40.2787 | 0 | 0.00035556 | 128.8761 | -9.1422e-05 | 0.0010667 | 6.4438 | -0.00027426 | 6.4446 |  | 10.4446 | 4 | 10.4446 | 40.2787 | 20.1394 | 20 | 20 | 0.13937 | -0.40578
1632 | 27.2 | 1.9999 | 10.3997 | 2 | 10.4 | 40.2771 | 0 | 0.00026466 | 128.8764 | -9.0902e-05 | 0.00079399 | 6.4438 | -0.00027271 | 6.4443 |  | 10.4443 | 4 | 10.4443 | 40.2771 | 20.1386 | 20 | 20 | 0.13857 | -0.26722
1633 | 27.2167 | 1.9999 | 10.3998 | 2 | 10.4 | 40.2755 | 0 | 0.00017429 | 128.8766 | -9.0376e-05 | 0.00052286 | 6.4438 | -0.00027113 | 6.4441 |  | 10.4441 | 4 | 10.4441 | 40.2755 | 20.1377 | 20 | 20 | 0.13775 | -0.12947
1634 | 27.2333 | 2 | 10.3999 | 2 | 10.4 | 40.2739 | 0 | 8.4441e-05 | 128.8766 | -8.9845e-05 | 0.00025332 | 6.4438 | -0.00026953 | 6.4438 |  | 10.4438 | 4 | 10.4438 | 40.2739 | 20.1369 | 20 | 20 | 0.13693 | 0.0074607
1635 | 27.25 | 2 | 10.4 | 2 | 10.4 | 40.2722 | 0 | -4.8661e-06 | 128.8766 | -8.9307e-05 | -1.4598e-05 | 6.4438 | -0.00026792 | 6.4435 |  | 10.4435 | 4 | 10.4435 | 40.2722 | 20.1361 | 20 | 20 | 0.13609 | 0.14355
1636 | 27.2667 | 2 | 10.4001 | 2 | 10.4 | 40.2705 | 0 | -9.363e-05 | 128.8766 | -8.8764e-05 | -0.00028089 | 6.4438 | -0.00026629 | 6.4433 |  | 10.4433 | 4 | 10.4433 | 40.2705 | 20.1353 | 20 | 20 | 0.13525 | 0.2788
1637 | 27.2833 | 2.0001 | 10.4002 | 2 | 10.4 | 40.2688 | 0 | -0.00018184 | 128.8764 | -8.8215e-05 | -0.00054553 | 6.4438 | -0.00026464 | 6.443 |  | 10.443 | 4 | 10.443 | 40.2688 | 20.1344 | 20 | 20 | 0.1344 | 0.41321
1638 | 27.3 | 2.0001 | 10.4003 | 2 | 10.4 | 40.2671 | 0 | -0.0002695 | 128.8761 | -8.766e-05 | -0.00080851 | 6.4438 | -0.00026298 | 6.4427 |  | 10.4427 | 4 | 10.4427 | 40.2671 | 20.1335 | 20 | 20 | 0.13354 | 0.54675
1639 | 27.3167 | 2.0001 | 10.4004 | 2 | 10.4 | 40.2654 | 0 | -0.0003566 | 128.8757 | -8.71e-05 | -0.0010698 | 6.4438 | -0.0002613 | 6.4425 |  | 10.4425 | 4 | 10.4425 | 40.2654 | 20.1327 | 20 | 20 | 0.13268 | 0.67942
1640 | 27.3333 | 2.0001 | 10.4004 | 2 | 10.4 | 40.2636 | 0 | -0.00044314 | 128.8753 | -8.6535e-05 | -0.0013294 | 6.4438 | -0.0002596 | 6.4422 |  | 10.4422 | 4 | 10.4422 | 40.2636 | 20.1318 | 20 | 20 | 0.1318 | 0.81122
1641 | 27.35 | 2.0002 | 10.4005 | 2 | 10.4 | 40.2618 | 0 | -0.0005291 | 128.8748 | -8.5964e-05 | -0.0015873 | 6.4437 | -0.00025789 | 6.4419 |  | 10.4419 | 4 | 10.4419 | 40.2618 | 20.1309 | 20 | 20 | 0.13092 | 0.94214
1642 | 27.3667 | 2.0002 | 10.4006 | 2 | 10.4 | 40.2601 | 0 | -0.00061449 | 128.8742 | -8.5388e-05 | -0.0018435 | 6.4437 | -0.00025616 | 6.4416 |  | 10.4416 | 4 | 10.4416 | 40.2601 | 20.13 | 20 | 20 | 0.13003 | 1.0722
1643 | 27.3833 | 2.0002 | 10.4007 | 2 | 10.4 | 40.2583 | 0 | -0.0006993 | 128.8735 | -8.4806e-05 | -0.0020979 | 6.4437 | -0.00025442 | 6.4413 |  | 10.4413 | 4 | 10.4413 | 40.2583 | 20.1291 | 20 | 20 | 0.12913 | 1.2013
1644 | 27.4 | 2.0002 | 10.4008 | 2 | 10.4 | 40.2564 | 0 | -0.00078352 | 128.8727 | -8.422e-05 | -0.0023506 | 6.4436 | -0.00025266 | 6.441 |  | 10.441 | 4 | 10.441 | 40.2564 | 20.1282 | 20 | 20 | 0.12822 | 1.3295
1645 | 27.4167 | 2.0003 | 10.4009 | 2 | 10.4 | 40.2546 | 0 | -0.00086715 | 128.8718 | -8.3629e-05 | -0.0026014 | 6.4436 | -0.00025089 | 6.4407 |  | 10.4407 | 4 | 10.4407 | 40.2546 | 20.1273 | 20 | 20 | 0.12731 | 1.4568
1646 | 27.4333 | 2.0003 | 10.401 | 2 | 10.4 | 40.2528 | 0 | -0.00095018 | 128.8709 | -8.3033e-05 | -0.0028505 | 6.4435 | -0.0002491 | 6.4404 |  | 10.4404 | 4 | 10.4404 | 40.2528 | 20.1264 | 20 | 20 | 0.12638 | 1.5832
1647 | 27.45 | 2.0003 | 10.401 | 2 | 10.4 | 40.2509 | 0 | -0.0010326 | 128.8698 | -8.2432e-05 | -0.0030978 | 6.4435 | -0.0002473 | 6.4401 |  | 10.4401 | 4 | 10.4401 | 40.2509 | 20.1255 | 20 | 20 | 0.12546 | 1.7087
1648 | 27.4667 | 2.0003 | 10.4011 | 2 | 10.4 | 40.249 | 0 | -0.0011144 | 128.8687 | -8.1826e-05 | -0.0033433 | 6.4434 | -0.00024548 | 6.4398 |  | 10.4398 | 4 | 10.4398 | 40.249 | 20.1245 | 20 | 20 | 0.12452 | 1.8332
1649 | 27.4833 | 2.0004 | 10.4012 | 2 | 10.4 | 40.2472 | 0 | -0.0011957 | 128.8675 | -8.1216e-05 | -0.003587 | 6.4434 | -0.00024365 | 6.4395 |  | 10.4395 | 4 | 10.4395 | 40.2472 | 20.1236 | 20 | 20 | 0.12358 | 1.9568
1650 | 27.5 | 2.0004 | 10.4013 | 2 | 10.4 | 40.2453 | 0 | -0.0012763 | 128.8662 | -8.0601e-05 | -0.0038288 | 6.4433 | -0.0002418 | 6.4392 |  | 10.4392 | 4 | 10.4392 | 40.2453 | 20.1226 | 20 | 20 | 0.12263 | 2.0794
1651 | 27.5167 | 2.0004 | 10.4014 | 2 | 10.4 | 40.2433 | 0 | -0.0013562 | 128.8649 | -7.9982e-05 | -0.0040687 | 6.4432 | -0.00023995 | 6.4389 |  | 10.4389 | 4 | 10.4389 | 40.2433 | 20.1217 | 20 | 20 | 0.12167 | 2.2011
1652 | 27.5333 | 2.0004 | 10.4014 | 2 | 10.4 | 40.2414 | 0 | -0.0014356 | 128.8634 | -7.9359e-05 | -0.0043068 | 6.4432 | -0.00023808 | 6.4386 |  | 10.4386 | 4 | 10.4386 | 40.2414 | 20.1207 | 20 | 20 | 0.12071 | 2.3218
1653 | 27.55 | 2.0005 | 10.4015 | 2 | 10.4 | 40.2395 | 0 | -0.0015143 | 128.8619 | -7.8731e-05 | -0.004543 | 6.4431 | -0.00023619 | 6.4383 |  | 10.4383 | 4 | 10.4383 | 40.2395 | 20.1197 | 20 | 20 | 0.11974 | 2.4415
1654 | 27.5667 | 2.0005 | 10.4016 | 2 | 10.4 | 40.2375 | 0 | -0.0015924 | 128.8603 | -7.8099e-05 | -0.0047773 | 6.443 | -0.0002343 | 6.438 |  | 10.438 | 4 | 10.438 | 40.2375 | 20.1188 | 20 | 20 | 0.11877 | 2.5603
1655 | 27.5833 | 2.0005 | 10.4017 | 2 | 10.4 | 40.2356 | 0 | -0.0016699 | 128.8587 | -7.7463e-05 | -0.0050097 | 6.4429 | -0.00023239 | 6.4377 |  | 10.4377 | 4 | 10.4377 | 40.2356 | 20.1178 | 20 | 20 | 0.11779 | 2.6781
1656 | 27.6 | 2.0005 | 10.4017 | 2 | 10.4 | 40.2336 | 0 | -0.0017467 | 128.8569 | -7.6823e-05 | -0.0052401 | 6.4428 | -0.00023047 | 6.4374 |  | 10.4374 | 4 | 10.4374 | 40.2336 | 20.1168 | 20 | 20 | 0.1168 | 2.7949
1657 | 27.6167 | 2.0006 | 10.4018 | 2 | 10.4 | 40.2316 | 0 | -0.0018229 | 128.8551 | -7.6179e-05 | -0.0054687 | 6.4428 | -0.00022854 | 6.4371 |  | 10.4371 | 4 | 10.4371 | 40.2316 | 20.1158 | 20 | 20 | 0.11581 | 2.9107
1658 | 27.6333 | 2.0006 | 10.4019 | 2 | 10.4 | 40.2296 | 0 | -0.0018984 | 128.8532 | -7.5532e-05 | -0.0056953 | 6.4427 | -0.0002266 | 6.4367 |  | 10.4367 | 4 | 10.4367 | 40.2296 | 20.1148 | 20 | 20 | 0.11481 | 3.0255
1659 | 27.65 | 2.0006 | 10.402 | 2 | 10.4 | 40.2276 | 0 | -0.0019733 | 128.8512 | -7.488e-05 | -0.0059199 | 6.4426 | -0.00022464 | 6.4364 |  | 10.4364 | 4 | 10.4364 | 40.2276 | 20.1138 | 20 | 20 | 0.1138 | 3.1393
1660 | 27.6667 | 2.0006 | 10.402 | 2 | 10.4 | 40.2256 | 0 | -0.0020475 | 128.8492 | -7.4225e-05 | -0.0061426 | 6.4425 | -0.00022268 | 6.4361 |  | 10.4361 | 4 | 10.4361 | 40.2256 | 20.1128 | 20 | 20 | 0.11279 | 3.2521
1661 | 27.6833 | 2.0007 | 10.4021 | 2 | 10.4 | 40.2236 | 0 | -0.0021211 | 128.8471 | -7.3567e-05 | -0.0063633 | 6.4424 | -0.0002207 | 6.4358 |  | 10.4358 | 4 | 10.4358 | 40.2236 | 20.1118 | 20 | 20 | 0.11178 | 3.3638
1662 | 27.7 | 2.0007 | 10.4022 | 2 | 10.4 | 40.2215 | 0 | -0.002194 | 128.8449 | -7.2905e-05 | -0.006582 | 6.4422 | -0.00021871 | 6.4354 |  | 10.4354 | 4 | 10.4354 | 40.2215 | 20.1108 | 20 | 20 | 0.11076 | 3.4746
1663 | 27.7167 | 2.0007 | 10.4023 | 2 | 10.4 | 40.2195 | 0 | -0.0022662 | 128.8426 | -7.224e-05 | -0.0067987 | 6.4421 | -0.00021672 | 6.4351 |  | 10.4351 | 4 | 10.4351 | 40.2195 | 20.1097 | 20 | 20 | 0.10973 | 3.5843
1664 | 27.7333 | 2.0007 | 10.4023 | 2 | 10.4 | 40.2174 | 0 | -0.0023378 | 128.8403 | -7.1571e-05 | -0.0070134 | 6.442 | -0.00021471 | 6.4348 |  | 10.4348 | 4 | 10.4348 | 40.2174 | 20.1087 | 20 | 20 | 0.1087 | 3.693
1665 | 27.75 | 2.0008 | 10.4024 | 2 | 10.4 | 40.2153 | 0 | -0.0024087 | 128.8379 | -7.0899e-05 | -0.0072261 | 6.4419 | -0.0002127 | 6.4345 |  | 10.4345 | 4 | 10.4345 | 40.2153 | 20.1077 | 20 | 20 | 0.10767 | 3.8007
1666 | 27.7667 | 2.0008 | 10.4025 | 2 | 10.4 | 40.2133 | 0 | -0.0024789 | 128.8354 | -7.0224e-05 | -0.0074368 | 6.4418 | -0.00021067 | 6.4341 |  | 10.4341 | 4 | 10.4341 | 40.2133 | 20.1066 | 20 | 20 | 0.10663 | 3.9073
1667 | 27.7833 | 2.0008 | 10.4025 | 2 | 10.4 | 40.2112 | 0 | -0.0025485 | 128.8328 | -6.9546e-05 | -0.0076454 | 6.4416 | -0.00020864 | 6.4338 |  | 10.4338 | 4 | 10.4338 | 40.2112 | 20.1056 | 20 | 20 | 0.10558 | 4.0129
1668 | 27.8 | 2.0008 | 10.4026 | 2 | 10.4 | 40.2091 | 0 | -0.0026173 | 128.8302 | -6.8866e-05 | -0.007852 | 6.4415 | -0.0002066 | 6.4335 |  | 10.4335 | 4 | 10.4335 | 40.2091 | 20.1045 | 20 | 20 | 0.10454 | 4.1175
1669 | 27.8167 | 2.0008 | 10.4027 | 2 | 10.4 | 40.207 | 0 | -0.0026855 | 128.8275 | -6.8182e-05 | -0.0080566 | 6.4414 | -0.00020455 | 6.4331 |  | 10.4331 | 4 | 10.4331 | 40.207 | 20.1035 | 20 | 20 | 0.10348 | 4.2209
1670 | 27.8333 | 2.0009 | 10.4028 | 2 | 10.4 | 40.2049 | 0 | -0.002753 | 128.8248 | -6.7495e-05 | -0.0082591 | 6.4412 | -0.00020249 | 6.4328 |  | 10.4328 | 4 | 10.4328 | 40.2049 | 20.1024 | 20 | 20 | 0.10243 | 4.3234
1671 | 27.85 | 2.0009 | 10.4028 | 2 | 10.4 | 40.2027 | 0 | -0.0028198 | 128.8219 | -6.6806e-05 | -0.0084595 | 6.4411 | -0.00020042 | 6.4324 |  | 10.4324 | 4 | 10.4324 | 40.2027 | 20.1014 | 20 | 20 | 0.10137 | 4.4247
1672 | 27.8667 | 2.0009 | 10.4029 | 2 | 10.4 | 40.2006 | 0 | -0.0028859 | 128.8191 | -6.6115e-05 | -0.0086578 | 6.441 | -0.00019834 | 6.4321 |  | 10.4321 | 4 | 10.4321 | 40.2006 | 20.1003 | 20 | 20 | 0.1003 | 4.525
1673 | 27.8833 | 2.0009 | 10.403 | 2 | 10.4 | 40.1985 | 0 | -0.0029514 | 128.8161 | -6.5421e-05 | -0.0088541 | 6.4408 | -0.00019626 | 6.4318 |  | 10.4318 | 4 | 10.4318 | 40.1985 | 20.0992 | 20 | 20 | 0.099235 | 4.6243
1674 | 27.9 | 2.0009 | 10.403 | 2 | 10.4 | 40.1963 | 0 | -0.0030161 | 128.8131 | -6.4724e-05 | -0.0090483 | 6.4407 | -0.00019417 | 6.4314 |  | 10.4314 | 4 | 10.4314 | 40.1963 | 20.0982 | 20 | 20 | 0.098164 | 4.7224
1675 | 27.9167 | 2.001 | 10.4031 | 2 | 10.4 | 40.1942 | 0 | -0.0030801 | 128.81 | -6.4025e-05 | -0.0092403 | 6.4405 | -0.00019208 | 6.4311 |  | 10.4311 | 4 | 10.4311 | 40.1942 | 20.0971 | 20 | 20 | 0.097089 | 4.8195
1676 | 27.9333 | 2.001 | 10.4031 | 2 | 10.4 | 40.192 | 0 | -0.0031434 | 128.8069 | -6.3324e-05 | -0.0094303 | 6.4403 | -0.00018997 | 6.4307 |  | 10.4307 | 4 | 10.4307 | 40.192 | 20.096 | 20 | 20 | 0.09601 | 4.9155
1677 | 27.95 | 2.001 | 10.4032 | 2 | 10.4 | 40.1899 | 0 | -0.0032061 | 128.8037 | -6.2621e-05 | -0.0096182 | 6.4402 | -0.00018786 | 6.4304 |  | 10.4304 | 4 | 10.4304 | 40.1899 | 20.0949 | 20 | 20 | 0.094929 | 5.0105
1678 | 27.9667 | 2.001 | 10.4033 | 2 | 10.4 | 40.1877 | 0 | -0.003268 | 128.8004 | -6.1915e-05 | -0.0098039 | 6.44 | -0.00018575 | 6.43 |  | 10.43 | 4 | 10.43 | 40.1877 | 20.0938 | 20 | 20 | 0.093844 | 5.1043
1679 | 27.9833 | 2.001 | 10.4033 | 2 | 10.4 | 40.1855 | 0 | -0.0033292 | 128.7971 | -6.1208e-05 | -0.0099876 | 6.4399 | -0.00018362 | 6.4297 |  | 10.4297 | 4 | 10.4297 | 40.1855 | 20.0928 | 20 | 20 | 0.092757 | 5.1971
1680 | 28 | 2.0011 | 10.4034 | 2 | 10.4 | 40.1833 | 0 | -0.0033897 | 128.7937 | -6.0499e-05 | -0.010169 | 6.4397 | -0.0001815 | 6.4293 |  | 10.4293 | 4 | 10.4293 | 40.1833 | 20.0917 | 20 | 20 | 0.091667 | 5.2887
1681 | 28.0167 | 2.0011 | 10.4034 | 2 | 10.4 | 40.1811 | 0 | -0.0034495 | 128.7902 | -5.9788e-05 | -0.010348 | 6.4395 | -0.00017936 | 6.429 |  | 10.429 | 4 | 10.429 | 40.1811 | 20.0906 | 20 | 20 | 0.090574 | 5.3793
1682 | 28.0333 | 2.0011 | 10.4035 | 2 | 10.4 | 40.179 | 0 | -0.0035085 | 128.7867 | -5.9075e-05 | -0.010526 | 6.4393 | -0.00017723 | 6.4286 |  | 10.4286 | 4 | 10.4286 | 40.179 | 20.0895 | 20 | 20 | 0.089479 | 5.4688
1683 | 28.05 | 2.0011 | 10.4036 | 2 | 10.4 | 40.1768 | 0 | -0.0035669 | 128.7832 | -5.8361e-05 | -0.010701 | 6.4392 | -0.00017508 | 6.4283 |  | 10.4283 | 4 | 10.4283 | 40.1768 | 20.0884 | 20 | 20 | 0.088381 | 5.5572
1684 | 28.0667 | 2.0011 | 10.4036 | 2 | 10.4 | 40.1746 | 0 | -0.0036246 | 128.7795 | -5.7645e-05 | -0.010874 | 6.439 | -0.00017293 | 6.4279 |  | 10.4279 | 4 | 10.4279 | 40.1746 | 20.0873 | 20 | 20 | 0.087281 | 5.6445
1685 | 28.0833 | 2.0012 | 10.4037 | 2 | 10.4 | 40.1724 | 0 | -0.0036815 | 128.7758 | -5.6927e-05 | -0.011044 | 6.4388 | -0.00017078 | 6.4276 |  | 10.4276 | 4 | 10.4276 | 40.1724 | 20.0862 | 20 | 20 | 0.086179 | 5.7306
1686 | 28.1 | 2.0012 | 10.4037 | 2 | 10.4 | 40.1701 | 0 | -0.0037377 | 128.7721 | -5.6208e-05 | -0.011213 | 6.4386 | -0.00016862 | 6.4272 |  | 10.4272 | 4 | 10.4272 | 40.1701 | 20.0851 | 20 | 20 | 0.085074 | 5.8157
1687 | 28.1167 | 2.0012 | 10.4038 | 2 | 10.4 | 40.1679 | 0 | -0.0037932 | 128.7683 | -5.5488e-05 | -0.01138 | 6.4384 | -0.00016646 | 6.4269 |  | 10.4269 | 4 | 10.4269 | 40.1679 | 20.084 | 20 | 20 | 0.083968 | 5.8997
1688 | 28.1333 | 2.0012 | 10.4038 | 2 | 10.4 | 40.1657 | 0 | -0.0038479 | 128.7645 | -5.4767e-05 | -0.011544 | 6.4382 | -0.0001643 | 6.4265 |  | 10.4265 | 4 | 10.4265 | 40.1657 | 20.0829 | 20 | 20 | 0.08286 | 5.9825
1689 | 28.15 | 2.0012 | 10.4039 | 2 | 10.4 | 40.1635 | 0 | -0.003902 | 128.7606 | -5.4044e-05 | -0.011706 | 6.438 | -0.00016213 | 6.4262 |  | 10.4262 | 4 | 10.4262 | 40.1635 | 20.0818 | 20 | 20 | 0.081751 | 6.0643
1690 | 28.1667 | 2.0012 | 10.404 | 2 | 10.4 | 40.1613 | 0 | -0.0039553 | 128.7566 | -5.332e-05 | -0.011866 | 6.4378 | -0.00015996 | 6.4258 |  | 10.4258 | 4 | 10.4258 | 40.1613 | 20.0806 | 20 | 20 | 0.08064 | 6.1449
1691 | 28.1833 | 2.0013 | 10.404 | 2 | 10.4 | 40.1591 | 0 | -0.0040079 | 128.7526 | -5.2596e-05 | -0.012024 | 6.4376 | -0.00015779 | 6.4254 |  | 10.4254 | 4 | 10.4254 | 40.1591 | 20.0795 | 20 | 20 | 0.079527 | 6.2245
1692 | 28.2 | 2.0013 | 10.4041 | 2 | 10.4 | 40.1568 | 0 | -0.0040598 | 128.7485 | -5.187e-05 | -0.012179 | 6.4374 | -0.00015561 | 6.4251 |  | 10.4251 | 4 | 10.4251 | 40.1568 | 20.0784 | 20 | 20 | 0.078413 | 6.3029
1693 | 28.2167 | 2.0013 | 10.4041 | 2 | 10.4 | 40.1546 | 0 | -0.0041109 | 128.7444 | -5.1144e-05 | -0.012333 | 6.4372 | -0.00015343 | 6.4247 |  | 10.4247 | 4 | 10.4247 | 40.1546 | 20.0773 | 20 | 20 | 0.077298 | 6.3802
1694 | 28.2333 | 2.0013 | 10.4042 | 2 | 10.4 | 40.1524 | 0 | -0.0041613 | 128.7403 | -5.0416e-05 | -0.012484 | 6.437 | -0.00015125 | 6.4244 |  | 10.4244 | 4 | 10.4244 | 40.1524 | 20.0762 | 20 | 20 | 0.076182 | 6.4563
1695 | 28.25 | 2.0013 | 10.4042 | 2 | 10.4 | 40.1501 | 0 | -0.004211 | 128.7361 | -4.9688e-05 | -0.012633 | 6.4368 | -0.00014907 | 6.424 |  | 10.424 | 4 | 10.424 | 40.1501 | 20.0751 | 20 | 20 | 0.075065 | 6.5314
1696 | 28.2667 | 2.0013 | 10.4043 | 2 | 10.4 | 40.1479 | 0 | -0.00426 | 128.7318 | -4.896e-05 | -0.01278 | 6.4366 | -0.00014688 | 6.4237 |  | 10.4237 | 4 | 10.4237 | 40.1479 | 20.0739 | 20 | 20 | 0.073948 | 6.6054
1697 | 28.2833 | 2.0013 | 10.4043 | 2 | 10.4 | 40.1457 | 0 | -0.0043082 | 128.7275 | -4.8231e-05 | -0.012925 | 6.4364 | -0.00014469 | 6.4233 |  | 10.4233 | 4 | 10.4233 | 40.1457 | 20.0728 | 20 | 20 | 0.072829 | 6.6782
1698 | 28.3 | 2.0014 | 10.4044 | 2 | 10.4 | 40.1434 | 0 | -0.0043557 | 128.7231 | -4.7501e-05 | -0.013067 | 6.4362 | -0.0001425 | 6.4229 |  | 10.4229 | 4 | 10.4229 | 40.1434 | 20.0717 | 20 | 20 | 0.07171 | 6.7499
1699 | 28.3167 | 2.0014 | 10.4044 | 2 | 10.4 | 40.1412 | 0 | -0.0044025 | 128.7187 | -4.6771e-05 | -0.013207 | 6.4359 | -0.00014031 | 6.4226 |  | 10.4226 | 4 | 10.4226 | 40.1412 | 20.0706 | 20 | 20 | 0.070591 | 6.8205
1700 | 28.3333 | 2.0014 | 10.4044 | 2 | 10.4 | 40.1389 | 0 | -0.0044485 | 128.7143 | -4.6041e-05 | -0.013346 | 6.4357 | -0.00013812 | 6.4222 |  | 10.4222 | 4 | 10.4222 | 40.1389 | 20.0695 | 20 | 20 | 0.069471 | 6.89
1701 | 28.35 | 2.0014 | 10.4045 | 2 | 10.4 | 40.1367 | 0 | -0.0044938 | 128.7098 | -4.5311e-05 | -0.013482 | 6.4355 | -0.00013593 | 6.4219 |  | 10.4219 | 4 | 10.4219 | 40.1367 | 20.0684 | 20 | 20 | 0.068351 | 6.9583
1702 | 28.3667 | 2.0014 | 10.4045 | 2 | 10.4 | 40.1345 | 0 | -0.0045384 | 128.7053 | -4.458e-05 | -0.013615 | 6.4353 | -0.00013374 | 6.4215 |  | 10.4215 | 4 | 10.4215 | 40.1345 | 20.0672 | 20 | 20 | 0.06723 | 7.0255
1703 | 28.3833 | 2.0014 | 10.4046 | 2 | 10.4 | 40.1322 | 0 | -0.0045823 | 128.7007 | -4.385e-05 | -0.013747 | 6.435 | -0.00013155 | 6.4212 |  | 10.4212 | 4 | 10.4212 | 40.1322 | 20.0661 | 20 | 20 | 0.06611 | 7.0917
1704 | 28.4 | 2.0014 | 10.4046 | 2 | 10.4 | 40.13 | 0 | -0.0046254 | 128.696 | -4.3119e-05 | -0.013876 | 6.4348 | -0.00012936 | 6.4208 |  | 10.4208 | 4 | 10.4208 | 40.13 | 20.065 | 20 | 20 | 0.06499 | 7.1566
1705 | 28.4167 | 2.0015 | 10.4047 | 2 | 10.4 | 40.1277 | 0 | -0.0046678 | 128.6914 | -4.2388e-05 | -0.014003 | 6.4346 | -0.00012717 | 6.4204 |  | 10.4204 | 4 | 10.4204 | 40.1277 | 20.0639 | 20 | 20 | 0.06387 | 7.2205
1706 | 28.4333 | 2.0015 | 10.4047 | 2 | 10.4 | 40.1255 | 0 | -0.0047094 | 128.6867 | -4.1658e-05 | -0.014128 | 6.4343 | -0.00012497 | 6.4201 |  | 10.4201 | 4 | 10.4201 | 40.1255 | 20.0628 | 20 | 20 | 0.062751 | 7.2833
1707 | 28.45 | 2.0015 | 10.4048 | 2 | 10.4 | 40.1233 | 0 | -0.0047504 | 128.6819 | -4.0928e-05 | -0.014251 | 6.4341 | -0.00012278 | 6.4197 |  | 10.4197 | 4 | 10.4197 | 40.1233 | 20.0616 | 20 | 20 | 0.061632 | 7.3449
1708 | 28.4667 | 2.0015 | 10.4048 | 2 | 10.4 | 40.121 | 0 | -0.0047906 | 128.6771 | -4.0198e-05 | -0.014372 | 6.4339 | -0.00012059 | 6.4194 |  | 10.4194 | 4 | 10.4194 | 40.121 | 20.0605 | 20 | 20 | 0.060513 | 7.4054
1709 | 28.4833 | 2.0015 | 10.4048 | 2 | 10.4 | 40.1188 | 0 | -0.00483 | 128.6723 | -3.9468e-05 | -0.01449 | 6.4336 | -0.0001184 | 6.419 |  | 10.419 | 4 | 10.419 | 40.1188 | 20.0594 | 20 | 20 | 0.059395 | 7.4648
1710 | 28.5 | 2.0015 | 10.4049 | 2 | 10.4 | 40.1166 | 0 | -0.0048688 | 128.6674 | -3.8739e-05 | -0.014606 | 6.4334 | -0.00011622 | 6.4186 |  | 10.4186 | 4 | 10.4186 | 40.1166 | 20.0583 | 20 | 20 | 0.058278 | 7.5231
1711 | 28.5167 | 2.0015 | 10.4049 | 2 | 10.4 | 40.1143 | 0 | -0.0049068 | 128.6625 | -3.8011e-05 | -0.01472 | 6.4331 | -0.00011403 | 6.4183 |  | 10.4183 | 4 | 10.4183 | 40.1143 | 20.0572 | 20 | 20 | 0.057162 | 7.5802
1712 | 28.5333 | 2.0015 | 10.4049 | 2 | 10.4 | 40.1121 | 0 | -0.0049441 | 128.6576 | -3.7283e-05 | -0.014832 | 6.4329 | -0.00011185 | 6.4179 |  | 10.4179 | 4 | 10.4179 | 40.1121 | 20.056 | 20 | 20 | 0.056047 | 7.6363
1713 | 28.55 | 2.0016 | 10.405 | 2 | 10.4 | 40.1099 | 0 | -0.0049806 | 128.6526 | -3.6555e-05 | -0.014942 | 6.4326 | -0.00010967 | 6.4176 |  | 10.4176 | 4 | 10.4176 | 40.1099 | 20.0549 | 20 | 20 | 0.054932 | 7.6912
1714 | 28.5667 | 2.0016 | 10.405 | 2 | 10.4 | 40.1076 | 0 | -0.0050164 | 128.6476 | -3.5829e-05 | -0.015049 | 6.4324 | -0.00010749 | 6.4172 |  | 10.4172 | 4 | 10.4172 | 40.1076 | 20.0538 | 20 | 20 | 0.05382 | 7.745
1715 | 28.5833 | 2.0016 | 10.4051 | 2 | 10.4 | 40.1054 | 0 | -0.0050515 | 128.6425 | -3.5103e-05 | -0.015155 | 6.4321 | -0.00010531 | 6.4169 |  | 10.4169 | 4 | 10.4169 | 40.1054 | 20.0527 | 20 | 20 | 0.052708 | 7.7977
1716 | 28.6 | 2.0016 | 10.4051 | 2 | 10.4 | 40.1032 | 0 | -0.0050859 | 128.6374 | -3.4378e-05 | -0.015258 | 6.4319 | -0.00010313 | 6.4165 |  | 10.4165 | 4 | 10.4165 | 40.1032 | 20.0516 | 20 | 20 | 0.051598 | 7.8493
1717 | 28.6167 | 2.0016 | 10.4051 | 2 | 10.4 | 40.101 | 0 | -0.0051196 | 128.6323 | -3.3654e-05 | -0.015359 | 6.4316 | -0.00010096 | 6.4162 |  | 10.4162 | 4 | 10.4162 | 40.101 | 20.0505 | 20 | 20 | 0.050489 | 7.8998
1718 | 28.6333 | 2.0016 | 10.4052 | 2 | 10.4 | 40.0988 | 0 | -0.0051525 | 128.6272 | -3.2931e-05 | -0.015458 | 6.4314 | -9.8792e-05 | 6.4158 |  | 10.4158 | 4 | 10.4158 | 40.0988 | 20.0494 | 20 | 20 | 0.049382 | 7.9492
1719 | 28.65 | 2.0016 | 10.4052 | 2 | 10.4 | 40.0966 | 0 | -0.0051847 | 128.622 | -3.2208e-05 | -0.015554 | 6.4311 | -9.6625e-05 | 6.4154 |  | 10.4154 | 4 | 10.4154 | 40.0966 | 20.0483 | 20 | 20 | 0.048277 | 7.9975
1720 | 28.6667 | 2.0016 | 10.4052 | 2 | 10.4 | 40.0943 | 0 | -0.0052162 | 128.6168 | -3.1488e-05 | -0.015649 | 6.4308 | -9.4463e-05 | 6.4151 |  | 10.4151 | 4 | 10.4151 | 40.0943 | 20.0472 | 20 | 20 | 0.047173 | 8.0447
1721 | 28.6833 | 2.0016 | 10.4052 | 2 | 10.4 | 40.0921 | 0 | -0.005247 | 128.6115 | -3.0768e-05 | -0.015741 | 6.4306 | -9.2304e-05 | 6.4147 |  | 10.4147 | 4 | 10.4147 | 40.0921 | 20.0461 | 20 | 20 | 0.046072 | 8.0907
1722 | 28.7 | 2.0016 | 10.4053 | 2 | 10.4 | 40.0899 | 0 | -0.005277 | 128.6062 | -3.0049e-05 | -0.015831 | 6.4303 | -9.0148e-05 | 6.4144 |  | 10.4144 | 4 | 10.4144 | 40.0899 | 20.045 | 20 | 20 | 0.044972 | 8.1357
1723 | 28.7167 | 2.0017 | 10.4053 | 2 | 10.4 | 40.0877 | 0 | -0.0053064 | 128.6009 | -2.9332e-05 | -0.015919 | 6.43 | -8.7997e-05 | 6.414 |  | 10.414 | 4 | 10.414 | 40.0877 | 20.0439 | 20 | 20 | 0.043875 | 8.1796
1724 | 28.7333 | 2.0017 | 10.4053 | 2 | 10.4 | 40.0856 | 0 | -0.005335 | 128.5956 | -2.8617e-05 | -0.016005 | 6.4298 | -8.585e-05 | 6.4137 |  | 10.4137 | 4 | 10.4137 | 40.0856 | 20.0428 | 20 | 20 | 0.04278 | 8.2224
1725 | 28.75 | 2.0017 | 10.4054 | 2 | 10.4 | 40.0834 | 0 | -0.0053629 | 128.5902 | -2.7902e-05 | -0.016089 | 6.4295 | -8.3707e-05 | 6.4133 |  | 10.4133 | 4 | 10.4133 | 40.0834 | 20.0417 | 20 | 20 | 0.041687 | 8.2641
1726 | 28.7667 | 2.0017 | 10.4054 | 2 | 10.4 | 40.0812 | 0 | -0.0053901 | 128.5849 | -2.7189e-05 | -0.01617 | 6.4292 | -8.1568e-05 | 6.413 |  | 10.413 | 4 | 10.413 | 40.0812 | 20.0406 | 20 | 20 | 0.040597 | 8.3047
1727 | 28.7833 | 2.0017 | 10.4054 | 2 | 10.4 | 40.079 | 0 | -0.0054165 | 128.5794 | -2.6478e-05 | -0.01625 | 6.429 | -7.9435e-05 | 6.4126 |  | 10.4126 | 4 | 10.4126 | 40.079 | 20.0395 | 20 | 20 | 0.039509 | 8.3442
1728 | 28.8 | 2.0017 | 10.4054 | 2 | 10.4 | 40.0768 | 0 | -0.0054423 | 128.574 | -2.5769e-05 | -0.016327 | 6.4287 | -7.7306e-05 | 6.4123 |  | 10.4123 | 4 | 10.4123 | 40.0768 | 20.0384 | 20 | 20 | 0.038423 | 8.3826
1729 | 28.8167 | 2.0017 | 10.4055 | 2 | 10.4 | 40.0747 | 0 | -0.0054674 | 128.5685 | -2.5061e-05 | -0.016402 | 6.4284 | -7.5183e-05 | 6.4119 |  | 10.4119 | 4 | 10.4119 | 40.0747 | 20.0373 | 20 | 20 | 0.037341 | 8.4199
1730 | 28.8333 | 2.0017 | 10.4055 | 2 | 10.4 | 40.0725 | 0 | -0.0054917 | 128.563 | -2.4355e-05 | -0.016475 | 6.4282 | -7.3064e-05 | 6.4116 |  | 10.4116 | 4 | 10.4116 | 40.0725 | 20.0363 | 20 | 20 | 0.036261 | 8.4562
1731 | 28.85 | 2.0017 | 10.4055 | 2 | 10.4 | 40.0704 | 0 | -0.0055154 | 128.5575 | -2.365e-05 | -0.016546 | 6.4279 | -7.0951e-05 | 6.4113 |  | 10.4113 | 4 | 10.4113 | 40.0704 | 20.0352 | 20 | 20 | 0.035184 | 8.4914
1732 | 28.8667 | 2.0017 | 10.4055 | 2 | 10.4 | 40.0682 | 0 | -0.0055383 | 128.552 | -2.2948e-05 | -0.016615 | 6.4276 | -6.8844e-05 | 6.4109 |  | 10.4109 | 4 | 10.4109 | 40.0682 | 20.0341 | 20 | 20 | 0.03411 | 8.5255
1733 | 28.8833 | 2.0017 | 10.4056 | 2 | 10.4 | 40.0661 | 0 | -0.0055606 | 128.5464 | -2.2248e-05 | -0.016682 | 6.4273 | -6.6743e-05 | 6.4106 |  | 10.4106 | 4 | 10.4106 | 40.0661 | 20.033 | 20 | 20 | 0.033039 | 8.5585
1734 | 28.9 | 2.0017 | 10.4056 | 2 | 10.4 | 40.0639 | 0 | -0.0055821 | 128.5408 | -2.1549e-05 | -0.016746 | 6.427 | -6.4648e-05 | 6.4102 |  | 10.4102 | 4 | 10.4102 | 40.0639 | 20.032 | 20 | 20 | 0.031972 | 8.5905
1735 | 28.9167 | 2.0018 | 10.4056 | 2 | 10.4 | 40.0618 | 0 | -0.005603 | 128.5352 | -2.0853e-05 | -0.016809 | 6.4268 | -6.2559e-05 | 6.4099 |  | 10.4099 | 4 | 10.4099 | 40.0618 | 20.0309 | 20 | 20 | 0.030907 | 8.6214
1736 | 28.9333 | 2.0018 | 10.4056 | 2 | 10.4 | 40.0597 | 0 | -0.0056231 | 128.5296 | -2.0159e-05 | -0.016869 | 6.4265 | -6.0476e-05 | 6.4096 |  | 10.4096 | 4 | 10.4096 | 40.0597 | 20.0298 | 20 | 20 | 0.029846 | 8.6512
1737 | 28.95 | 2.0018 | 10.4056 | 2 | 10.4 | 40.0576 | 0 | -0.0056426 | 128.524 | -1.9467e-05 | -0.016928 | 6.4262 | -5.84e-05 | 6.4092 |  | 10.4092 | 4 | 10.4092 | 40.0576 | 20.0288 | 20 | 20 | 0.028788 | 8.68
1738 | 28.9667 | 2.0018 | 10.4057 | 2 | 10.4 | 40.0555 | 0 | -0.0056614 | 128.5183 | -1.8777e-05 | -0.016984 | 6.4259 | -5.633e-05 | 6.4089 |  | 10.4089 | 4 | 10.4089 | 40.0555 | 20.0277 | 20 | 20 | 0.027734 | 8.7078
1739 | 28.9833 | 2.0018 | 10.4057 | 2 | 10.4 | 40.0534 | 0 | -0.0056795 | 128.5126 | -1.8089e-05 | -0.017038 | 6.4256 | -5.4267e-05 | 6.4085 |  | 10.4085 | 4 | 10.4085 | 40.0534 | 20.0267 | 20 | 20 | 0.026684 | 8.7344
1740 | 29 | 2.0018 | 10.4057 | 2 | 10.4 | 40.0513 | 0 | -0.0056969 | 128.5069 | -1.7404e-05 | -0.017091 | 6.4253 | -5.2212e-05 | 6.4082 |  | 10.4082 | 4 | 10.4082 | 40.0513 | 20.0256 | 20 | 20 | 0.025637 | 8.7601
1741 | 29.0167 | 2.0018 | 10.4057 | 2 | 10.4 | 40.0492 | 0 | -0.0057136 | 128.5012 | -1.6721e-05 | -0.017141 | 6.4251 | -5.0163e-05 | 6.4079 |  | 10.4079 | 4 | 10.4079 | 40.0492 | 20.0246 | 20 | 20 | 0.024594 | 8.7847
1742 | 29.0333 | 2.0018 | 10.4057 | 2 | 10.4 | 40.0471 | 0 | -0.0057296 | 128.4955 | -1.6041e-05 | -0.017189 | 6.4248 | -4.8122e-05 | 6.4075 |  | 10.4075 | 4 | 10.4075 | 40.0471 | 20.0236 | 20 | 20 | 0.023555 | 8.8082
1743 | 29.05 | 2.0018 | 10.4057 | 2 | 10.4 | 40.045 | 0 | -0.005745 | 128.4897 | -1.5363e-05 | -0.017235 | 6.4245 | -4.6089e-05 | 6.4072 |  | 10.4072 | 4 | 10.4072 | 40.045 | 20.0225 | 20 | 20 | 0.022519 | 8.8308
1744 | 29.0667 | 2.0018 | 10.4058 | 2 | 10.4 | 40.043 | 0 | -0.0057597 | 128.484 | -1.4688e-05 | -0.017279 | 6.4242 | -4.4063e-05 | 6.4069 |  | 10.4069 | 4 | 10.4069 | 40.043 | 20.0215 | 20 | 20 | 0.021488 | 8.8522
1745 | 29.0833 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0409 | 0 | -0.0057737 | 128.4782 | -1.4015e-05 | -0.017321 | 6.4239 | -4.2045e-05 | 6.4065 |  | 10.4065 | 4 | 10.4065 | 40.0409 | 20.0205 | 20 | 20 | 0.020461 | 8.8727
1746 | 29.1 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0389 | 0 | -0.005787 | 128.4724 | -1.3345e-05 | -0.017361 | 6.4236 | -4.0035e-05 | 6.4062 |  | 10.4062 | 4 | 10.4062 | 40.0389 | 20.0194 | 20 | 20 | 0.019438 | 8.8921
1747 | 29.1167 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0368 | 0 | -0.0057997 | 128.4666 | -1.2678e-05 | -0.017399 | 6.4233 | -3.8033e-05 | 6.4059 |  | 10.4059 | 4 | 10.4059 | 40.0368 | 20.0184 | 20 | 20 | 0.018419 | 8.9106
1748 | 29.1333 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0348 | 0 | -0.0058117 | 128.4608 | -1.2013e-05 | -0.017435 | 6.423 | -3.604e-05 | 6.4056 |  | 10.4056 | 4 | 10.4056 | 40.0348 | 20.0174 | 20 | 20 | 0.017404 | 8.928
1749 | 29.15 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0328 | 0 | -0.0058231 | 128.455 | -1.1352e-05 | -0.017469 | 6.4227 | -3.4055e-05 | 6.4052 |  | 10.4052 | 4 | 10.4052 | 40.0328 | 20.0164 | 20 | 20 | 0.016394 | 8.9444
1750 | 29.1667 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0308 | 0 | -0.0058338 | 128.4492 | -1.0693e-05 | -0.017501 | 6.4225 | -3.2078e-05 | 6.4049 |  | 10.4049 | 4 | 10.4049 | 40.0308 | 20.0154 | 20 | 20 | 0.015389 | 8.9597
1751 | 29.1833 | 2.0018 | 10.4058 | 2 | 10.4 | 40.0288 | 0 | -0.0058438 | 128.4433 | -1.0037e-05 | -0.017531 | 6.4222 | -3.0111e-05 | 6.4046 |  | 10.4046 | 4 | 10.4046 | 40.0288 | 20.0144 | 20 | 20 | 0.014388 | 8.9741
1752 | 29.2 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0268 | 0 | -0.0058532 | 128.4375 | -9.384e-06 | -0.01756 | 6.4219 | -2.8152e-05 | 6.4043 |  | 10.4043 | 4 | 10.4043 | 40.0268 | 20.0134 | 20 | 20 | 0.013391 | 8.9875
1753 | 29.2167 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0248 | 0 | -0.0058619 | 128.4316 | -8.7341e-06 | -0.017586 | 6.4216 | -2.6202e-05 | 6.404 |  | 10.404 | 4 | 10.404 | 40.0248 | 20.0124 | 20 | 20 | 0.012399 | 8.9999
1754 | 29.2333 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0228 | 0 | -0.00587 | 128.4257 | -8.0873e-06 | -0.01761 | 6.4213 | -2.4262e-05 | 6.4037 |  | 10.4037 | 4 | 10.4037 | 40.0228 | 20.0114 | 20 | 20 | 0.011413 | 9.0113
1755 | 29.25 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0209 | 0 | -0.0058775 | 128.4198 | -7.4436e-06 | -0.017632 | 6.421 | -2.2331e-05 | 6.4033 |  | 10.4033 | 4 | 10.4033 | 40.0209 | 20.0104 | 20 | 20 | 0.01043 | 9.0218
1756 | 29.2667 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0189 | 0 | -0.0058843 | 128.414 | -6.803e-06 | -0.017653 | 6.4207 | -2.0409e-05 | 6.403 |  | 10.403 | 4 | 10.403 | 40.0189 | 20.0095 | 20 | 20 | 0.0094532 | 9.0312
1757 | 29.2833 | 2.0018 | 10.4059 | 2 | 10.4 | 40.017 | 0 | -0.0058904 | 128.4081 | -6.1657e-06 | -0.017671 | 6.4204 | -1.8497e-05 | 6.4027 |  | 10.4027 | 4 | 10.4027 | 40.017 | 20.0085 | 20 | 20 | 0.008481 | 9.0397
1758 | 29.3 | 2.0018 | 10.4059 | 2 | 10.4 | 40.015 | 0 | -0.005896 | 128.4022 | -5.5316e-06 | -0.017688 | 6.4201 | -1.6595e-05 | 6.4024 |  | 10.4024 | 4 | 10.4024 | 40.015 | 20.0075 | 20 | 20 | 0.0075139 | 9.0472
1759 | 29.3167 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0131 | 0 | -0.0059009 | 128.3963 | -4.9008e-06 | -0.017703 | 6.4198 | -1.4702e-05 | 6.4021 |  | 10.4021 | 4 | 10.4021 | 40.0131 | 20.0066 | 20 | 20 | 0.0065518 | 9.0538
1760 | 29.3333 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0112 | 0 | -0.0059051 | 128.3904 | -4.2733e-06 | -0.017715 | 6.4195 | -1.282e-05 | 6.4018 |  | 10.4018 | 4 | 10.4018 | 40.0112 | 20.0056 | 20 | 20 | 0.005595 | 9.0594
1761 | 29.35 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0093 | 0 | -0.0059088 | 128.3845 | -3.6492e-06 | -0.017726 | 6.4192 | -1.0948e-05 | 6.4015 |  | 10.4015 | 4 | 10.4015 | 40.0093 | 20.0046 | 20 | 20 | 0.0046434 | 9.064
1762 | 29.3667 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0074 | 0 | -0.0059118 | 128.3786 | -3.0285e-06 | -0.017735 | 6.4189 | -9.0856e-06 | 6.4012 |  | 10.4012 | 4 | 10.4012 | 40.0074 | 20.0037 | 20 | 20 | 0.0036971 | 9.0677
1763 | 29.3833 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0055 | 0 | -0.0059142 | 128.3726 | -2.4113e-06 | -0.017743 | 6.4186 | -7.234e-06 | 6.4009 |  | 10.4009 | 4 | 10.4009 | 40.0055 | 20.0028 | 20 | 20 | 0.0027562 | 9.0705
1764 | 29.4 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0036 | 0 | -0.005916 | 128.3667 | -1.7976e-06 | -0.017748 | 6.4183 | -5.3929e-06 | 6.4006 |  | 10.4006 | 4 | 10.4006 | 40.0036 | 20.0018 | 20 | 20 | 0.0018207 | 9.0723
1765 | 29.4167 | 2.0018 | 10.4059 | 2 | 10.4 | 40.0018 | 0 | -0.0059172 | 128.3608 | -1.1875e-06 | -0.017752 | 6.418 | -3.5625e-06 | 6.4003 |  | 10.4003 | 4 | 10.4003 | 40.0018 | 20.0009 | 20 | 20 | 0.00089071 | 9.0732
1766 | 29.4333 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9999 | 0 | -0.0059178 | 128.3549 | -5.8094e-07 | -0.017753 | 6.4177 | -1.7428e-06 | 6.4 |  | 10.4 | 4 | 10.4 | 39.9999 | 20 | 20 | 20 | -3.3709e-05 | 9.0731
1767 | 29.45 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9981 | 0 | -0.0059178 | 128.349 | 2.1986e-08 | -0.017753 | 6.4174 | 6.5958e-08 | 6.3997 |  | 10.3997 | 4 | 10.3997 | 39.9981 | 19.999 | 20 | 20 | -0.0009525 | 9.0722
1768 | 29.4667 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9963 | 0 | -0.0059171 | 128.3431 | 6.2125e-07 | -0.017751 | 6.4172 | 1.8637e-06 | 6.3994 |  | 10.3994 | 4 | 10.3994 | 39.9963 | 19.9981 | 20 | 20 | -0.0018656 | 9.0703
1769 | 29.4833 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9945 | 0 | -0.0059159 | 128.3371 | 1.2168e-06 | -0.017748 | 6.4169 | 3.6504e-06 | 6.3991 |  | 10.3991 | 4 | 10.3991 | 39.9945 | 19.9972 | 20 | 20 | -0.002773 | 9.0675
1770 | 29.5 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9927 | 0 | -0.0059141 | 128.3312 | 1.8086e-06 | -0.017742 | 6.4166 | 5.4259e-06 | 6.3988 |  | 10.3988 | 4 | 10.3988 | 39.9927 | 19.9963 | 20 | 20 | -0.0036746 | 9.0639
1771 | 29.5167 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9909 | 0 | -0.0059117 | 128.3253 | 2.3967e-06 | -0.017735 | 6.4163 | 7.19e-06 | 6.3985 |  | 10.3985 | 4 | 10.3985 | 39.9909 | 19.9954 | 20 | 20 | -0.0045703 | 9.0593
1772 | 29.5333 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9891 | 0 | -0.0059087 | 128.3194 | 2.9809e-06 | -0.017726 | 6.416 | 8.9426e-06 | 6.3983 |  | 10.3983 | 4 | 10.3983 | 39.9891 | 19.9945 | 20 | 20 | -0.0054601 | 9.0538
1773 | 29.55 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9873 | 0 | -0.0059052 | 128.3135 | 3.5612e-06 | -0.017716 | 6.4157 | 1.0684e-05 | 6.398 |  | 10.398 | 4 | 10.398 | 39.9873 | 19.9937 | 20 | 20 | -0.006344 | 9.0475
1774 | 29.5667 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9856 | 0 | -0.005901 | 128.3076 | 4.1377e-06 | -0.017703 | 6.4154 | 1.2413e-05 | 6.3977 |  | 10.3977 | 4 | 10.3977 | 39.9856 | 19.9928 | 20 | 20 | -0.0072218 | 9.0403
1775 | 29.5833 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9838 | 0 | -0.0058963 | 128.3017 | 4.7103e-06 | -0.017689 | 6.4151 | 1.4131e-05 | 6.3974 |  | 10.3974 | 4 | 10.3974 | 39.9838 | 19.9919 | 20 | 20 | -0.0080936 | 9.0322
1776 | 29.6 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9821 | 0 | -0.0058911 | 128.2958 | 5.2789e-06 | -0.017673 | 6.4148 | 1.5837e-05 | 6.3971 |  | 10.3971 | 4 | 10.3971 | 39.9821 | 19.991 | 20 | 20 | -0.0089592 | 9.0232
1777 | 29.6167 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9804 | 0 | -0.0058852 | 128.2899 | 5.8435e-06 | -0.017656 | 6.4145 | 1.753e-05 | 6.3969 |  | 10.3969 | 4 | 10.3969 | 39.9804 | 19.9902 | 20 | 20 | -0.0098187 | 9.0134
1778 | 29.6333 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9787 | 0 | -0.0058788 | 128.284 | 6.4041e-06 | -0.017636 | 6.4142 | 1.9212e-05 | 6.3966 |  | 10.3966 | 4 | 10.3966 | 39.9787 | 19.9893 | 20 | 20 | -0.010672 | 9.0027
1779 | 29.65 | 2.0018 | 10.4059 | 2 | 10.4 | 39.977 | 0 | -0.0058718 | 128.2782 | 6.9606e-06 | -0.017616 | 6.4139 | 2.0882e-05 | 6.3963 |  | 10.3963 | 4 | 10.3963 | 39.977 | 19.9885 | 20 | 20 | -0.011519 | 8.9912
1780 | 29.6667 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9753 | 0 | -0.0058643 | 128.2723 | 7.513e-06 | -0.017593 | 6.4136 | 2.2539e-05 | 6.396 |  | 10.396 | 4 | 10.396 | 39.9753 | 19.9876 | 20 | 20 | -0.01236 | 8.9789
1781 | 29.6833 | 2.0018 | 10.4059 | 2 | 10.4 | 39.9736 | 0 | -0.0058563 | 128.2665 | 8.0613e-06 | -0.017569 | 6.4133 | 2.4184e-05 | 6.3958 |  | 10.3958 | 4 | 10.3958 | 39.9736 | 19.9868 | 20 | 20 | -0.013194 | 8.9657
1782 | 29.7 | 2.0018 | 10.4058 | 2 | 10.4 | 39.972 | 0 | -0.0058477 | 128.2606 | 8.6055e-06 | -0.017543 | 6.413 | 2.5817e-05 | 6.3955 |  | 10.3955 | 4 | 10.3955 | 39.972 | 19.986 | 20 | 20 | -0.014022 | 8.9516
1783 | 29.7167 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9703 | 0 | -0.0058385 | 128.2548 | 9.1455e-06 | -0.017516 | 6.4127 | 2.7437e-05 | 6.3953 |  | 10.3953 | 4 | 10.3953 | 39.9703 | 19.9852 | 20 | 20 | -0.014843 | 8.9368
1784 | 29.7333 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9687 | 0 | -0.0058288 | 128.2489 | 9.6813e-06 | -0.017487 | 6.4124 | 2.9044e-05 | 6.395 |  | 10.395 | 4 | 10.395 | 39.9687 | 19.9843 | 20 | 20 | -0.015658 | 8.9211
1785 | 29.75 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9671 | 0 | -0.0058186 | 128.2431 | 1.0213e-05 | -0.017456 | 6.4122 | 3.0639e-05 | 6.3947 |  | 10.3947 | 4 | 10.3947 | 39.9671 | 19.9835 | 20 | 20 | -0.016467 | 8.9047
1786 | 29.7667 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9655 | 0 | -0.0058079 | 128.2373 | 1.074e-05 | -0.017424 | 6.4119 | 3.222e-05 | 6.3945 |  | 10.3945 | 4 | 10.3945 | 39.9655 | 19.9827 | 20 | 20 | -0.017269 | 8.8874
1787 | 29.7833 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9639 | 0 | -0.0057966 | 128.2315 | 1.1263e-05 | -0.01739 | 6.4116 | 3.3789e-05 | 6.3942 |  | 10.3942 | 4 | 10.3942 | 39.9639 | 19.9819 | 20 | 20 | -0.018064 | 8.8693
1788 | 29.8 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9623 | 0 | -0.0057848 | 128.2257 | 1.1782e-05 | -0.017355 | 6.4113 | 3.5345e-05 | 6.394 |  | 10.394 | 4 | 10.394 | 39.9623 | 19.9811 | 20 | 20 | -0.018852 | 8.8505
1789 | 29.8167 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9607 | 0 | -0.0057725 | 128.22 | 1.2296e-05 | -0.017318 | 6.411 | 3.6888e-05 | 6.3937 |  | 10.3937 | 4 | 10.3937 | 39.9607 | 19.9804 | 20 | 20 | -0.019634 | 8.8308
1790 | 29.8333 | 2.0018 | 10.4058 | 2 | 10.4 | 39.9592 | 0 | -0.0057597 | 128.2142 | 1.2806e-05 | -0.017279 | 6.4107 | 3.8418e-05 | 6.3935 |  | 10.3935 | 4 | 10.3935 | 39.9592 | 19.9796 | 20 | 20 | -0.020409 | 8.8104
1791 | 29.85 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9576 | 0 | -0.0057464 | 128.2084 | 1.3312e-05 | -0.017239 | 6.4104 | 3.9935e-05 | 6.3932 |  | 10.3932 | 4 | 10.3932 | 39.9576 | 19.9788 | 20 | 20 | -0.021178 | 8.7893
1792 | 29.8667 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9561 | 0 | -0.0057326 | 128.2027 | 1.3813e-05 | -0.017198 | 6.4101 | 4.1438e-05 | 6.393 |  | 10.393 | 4 | 10.393 | 39.9561 | 19.9781 | 20 | 20 | -0.021939 | 8.7673
1793 | 29.8833 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9546 | 0 | -0.0057183 | 128.197 | 1.4309e-05 | -0.017155 | 6.4098 | 4.2928e-05 | 6.3927 |  | 10.3927 | 4 | 10.3927 | 39.9546 | 19.9773 | 20 | 20 | -0.022694 | 8.7446
1794 | 29.9 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9531 | 0 | -0.0057035 | 128.1913 | 1.4802e-05 | -0.017111 | 6.4096 | 4.4405e-05 | 6.3925 |  | 10.3925 | 4 | 10.3925 | 39.9531 | 19.9766 | 20 | 20 | -0.023442 | 8.7212
1795 | 29.9167 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9516 | 0 | -0.0056882 | 128.1856 | 1.5289e-05 | -0.017065 | 6.4093 | 4.5868e-05 | 6.3923 |  | 10.3923 | 4 | 10.3923 | 39.9516 | 19.9758 | 20 | 20 | -0.024183 | 8.697
1796 | 29.9333 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9502 | 0 | -0.0056724 | 128.1799 | 1.5773e-05 | -0.017017 | 6.409 | 4.7318e-05 | 6.392 |  | 10.392 | 4 | 10.392 | 39.9502 | 19.9751 | 20 | 20 | -0.024917 | 8.6721
1797 | 29.95 | 2.0018 | 10.4057 | 2 | 10.4 | 39.9487 | 0 | -0.0056562 | 128.1743 | 1.6251e-05 | -0.016969 | 6.4087 | 4.8754e-05 | 6.3918 |  | 10.3918 | 4 | 10.3918 | 39.9487 | 19.9744 | 20 | 20 | -0.025643 | 8.6464
1798 | 29.9667 | 2.0018 | 10.4056 | 2 | 10.4 | 39.9473 | 0 | -0.0056395 | 128.1686 | 1.6725e-05 | -0.016918 | 6.4084 | 5.0176e-05 | 6.3916 |  | 10.3916 | 4 | 10.3916 | 39.9473 | 19.9736 | 20 | 20 | -0.026363 | 8.6201
1799 | 29.9833 | 2.0018 | 10.4056 | 2 | 10.4 | 39.9458 | 0 | -0.0056223 | 128.163 | 1.7195e-05 | -0.016867 | 6.4082 | 5.1585e-05 | 6.3913 |  | 10.3913 | 4 | 10.3913 | 39.9458 | 19.9729 | 20 | 20 | -0.027076 | 8.593
1800 | 30 | 2.0018 | 10.4056 | 2 | 10.4 | 39.9444 | 0 | -0.0056046 | 128.1574 | 1.766e-05 | -0.016814 | 6.4079 | 5.298e-05 | 6.3911 |  | 10.3911 | 4 | 10.3911 | 39.9444 | 19.9722 | 20 | 20 | -0.027782 | 8.5652
1801 | 30.0167 | 2.0017 | 10.4056 | 2 | 10.4 | 39.943 | 0 | -0.0055865 | 128.1518 | 1.812e-05 | -0.016759 | 6.4076 | 5.4361e-05 | 6.3909 |  | 10.3909 | 4 | 10.3909 | 39.943 | 19.9715 | 20 | 20 | -0.028481 | 8.5367
1802 | 30.0333 | 2.0017 | 10.4056 | 2 | 10.4 | 39.9417 | 0 | -0.0055679 | 128.1463 | 1.8576e-05 | -0.016704 | 6.4073 | 5.5728e-05 | 6.3907 |  | 10.3907 | 4 | 10.3907 | 39.9417 | 19.9708 | 20 | 20 | -0.029172 | 8.5076
1803 | 30.05 | 2.0017 | 10.4055 | 2 | 10.4 | 39.9403 | 0 | -0.0055489 | 128.1407 | 1.9027e-05 | -0.016647 | 6.407 | 5.7081e-05 | 6.3904 |  | 10.3904 | 4 | 10.3904 | 39.9403 | 19.9701 | 20 | 20 | -0.029857 | 8.4777
1804 | 30.0667 | 2.0017 | 10.4055 | 2 | 10.4 | 39.9389 | 0 | -0.0055294 | 128.1352 | 1.9473e-05 | -0.016588 | 6.4068 | 5.842e-05 | 6.3902 |  | 10.3902 | 4 | 10.3902 | 39.9389 | 19.9695 | 20 | 20 | -0.030534 | 8.4472
1805 | 30.0833 | 2.0017 | 10.4055 | 2 | 10.4 | 39.9376 | 0 | -0.0055095 | 128.1297 | 1.9915e-05 | -0.016528 | 6.4065 | 5.9745e-05 | 6.39 |  | 10.39 | 4 | 10.39 | 39.9376 | 19.9688 | 20 | 20 | -0.031204 | 8.416
1806 | 30.1 | 2.0017 | 10.4055 | 2 | 10.4 | 39.9363 | 0 | -0.0054891 | 128.1242 | 2.0352e-05 | -0.016467 | 6.4062 | 6.1056e-05 | 6.3898 |  | 10.3898 | 4 | 10.3898 | 39.9363 | 19.9681 | 20 | 20 | -0.031867 | 8.3841
1807 | 30.1167 | 2.0017 | 10.4055 | 2 | 10.4 | 39.935 | 0 | -0.0054684 | 128.1187 | 2.0784e-05 | -0.016405 | 6.4059 | 6.2353e-05 | 6.3896 |  | 10.3896 | 4 | 10.3896 | 39.935 | 19.9675 | 20 | 20 | -0.032522 | 8.3516
1808 | 30.1333 | 2.0017 | 10.4054 | 2 | 10.4 | 39.9337 | 0 | -0.0054471 | 128.1133 | 2.1212e-05 | -0.016341 | 6.4057 | 6.3636e-05 | 6.3894 |  | 10.3894 | 4 | 10.3894 | 39.9337 | 19.9668 | 20 | 20 | -0.033171 | 8.3184
1809 | 30.15 | 2.0017 | 10.4054 | 2 | 10.4 | 39.9324 | 0 | -0.0054255 | 128.1078 | 2.1635e-05 | -0.016277 | 6.4054 | 6.4904e-05 | 6.3892 |  | 10.3892 | 4 | 10.3892 | 39.9324 | 19.9662 | 20 | 20 | -0.033811 | 8.2846
1810 | 30.1667 | 2.0017 | 10.4054 | 2 | 10.4 | 39.9311 | 0 | -0.0054035 | 128.1024 | 2.2053e-05 | -0.01621 | 6.4051 | 6.6159e-05 | 6.389 |  | 10.389 | 4 | 10.389 | 39.9311 | 19.9656 | 20 | 20 | -0.034445 | 8.2502
1811 | 30.1833 | 2.0017 | 10.4054 | 2 | 10.4 | 39.9299 | 0 | -0.005381 | 128.0971 | 2.2466e-05 | -0.016143 | 6.4049 | 6.7398e-05 | 6.3888 |  | 10.3888 | 4 | 10.3888 | 39.9299 | 19.9649 | 20 | 20 | -0.035071 | 8.2151
1812 | 30.2 | 2.0017 | 10.4054 | 2 | 10.4 | 39.9286 | 0 | -0.0053581 | 128.0917 | 2.2875e-05 | -0.016074 | 6.4046 | 6.8624e-05 | 6.3886 |  | 10.3886 | 4 | 10.3886 | 39.9286 | 19.9643 | 20 | 20 | -0.03569 | 8.1794
1813 | 30.2167 | 2.0017 | 10.4053 | 2 | 10.4 | 39.9274 | 0 | -0.0053348 | 128.0864 | 2.3278e-05 | -0.016005 | 6.4043 | 6.9835e-05 | 6.3884 |  | 10.3884 | 4 | 10.3884 | 39.9274 | 19.9637 | 20 | 20 | -0.036302 | 8.1431
1814 | 30.2333 | 2.0017 | 10.4053 | 2 | 10.4 | 39.9262 | 0 | -0.0053112 | 128.0811 | 2.3677e-05 | -0.015933 | 6.4041 | 7.1031e-05 | 6.3882 |  | 10.3882 | 4 | 10.3882 | 39.9262 | 19.9631 | 20 | 20 | -0.036906 | 8.1062
1815 | 30.25 | 2.0017 | 10.4053 | 2 | 10.4 | 39.925 | 0 | -0.0052871 | 128.0758 | 2.4071e-05 | -0.015861 | 6.4038 | 7.2214e-05 | 6.388 |  | 10.388 | 4 | 10.388 | 39.925 | 19.9625 | 20 | 20 | -0.037503 | 8.0687
1816 | 30.2667 | 2.0016 | 10.4053 | 2 | 10.4 | 39.9238 | 0 | -0.0052626 | 128.0705 | 2.446e-05 | -0.015788 | 6.4035 | 7.3381e-05 | 6.3878 |  | 10.3878 | 4 | 10.3878 | 39.9238 | 19.9619 | 20 | 20 | -0.038092 | 8.0306
1817 | 30.2833 | 2.0016 | 10.4052 | 2 | 10.4 | 39.9227 | 0 | -0.0052378 | 128.0653 | 2.4845e-05 | -0.015713 | 6.4033 | 7.4534e-05 | 6.3876 |  | 10.3876 | 4 | 10.3876 | 39.9227 | 19.9613 | 20 | 20 | -0.038674 | 7.9919
1818 | 30.3 | 2.0016 | 10.4052 | 2 | 10.4 | 39.9215 | 0 | -0.0052126 | 128.0601 | 2.5224e-05 | -0.015638 | 6.403 | 7.5673e-05 | 6.3874 |  | 10.3874 | 4 | 10.3874 | 39.9215 | 19.9608 | 20 | 20 | -0.039248 | 7.9527
1819 | 30.3167 | 2.0016 | 10.4052 | 2 | 10.4 | 39.9204 | 0 | -0.005187 | 128.0549 | 2.5599e-05 | -0.015561 | 6.4027 | 7.6797e-05 | 6.3873 |  | 10.3873 | 4 | 10.3873 | 39.9204 | 19.9602 | 20 | 20 | -0.039815 | 7.9129
1820 | 30.3333 | 2.0016 | 10.4052 | 2 | 10.4 | 39.9193 | 0 | -0.005161 | 128.0497 | 2.5969e-05 | -0.015483 | 6.4025 | 7.7906e-05 | 6.3871 |  | 10.3871 | 4 | 10.3871 | 39.9193 | 19.9596 | 20 | 20 | -0.040375 | 7.8725
1821 | 30.35 | 2.0016 | 10.4051 | 2 | 10.4 | 39.9181 | 0 | -0.0051347 | 128.0446 | 2.6334e-05 | -0.015404 | 6.4022 | 7.9001e-05 | 6.3869 |  | 10.3869 | 4 | 10.3869 | 39.9181 | 19.9591 | 20 | 20 | -0.040927 | 7.8316
1822 | 30.3667 | 2.0016 | 10.4051 | 2 | 10.4 | 39.9171 | 0 | -0.005108 | 128.0395 | 2.6694e-05 | -0.015324 | 6.402 | 8.0081e-05 | 6.3867 |  | 10.3867 | 4 | 10.3867 | 39.9171 | 19.9585 | 20 | 20 | -0.041471 | 7.7901
1823 | 30.3833 | 2.0016 | 10.4051 | 2 | 10.4 | 39.916 | 0 | -0.0050809 | 128.0344 | 2.7049e-05 | -0.015243 | 6.4017 | 8.1146e-05 | 6.3866 |  | 10.3866 | 4 | 10.3866 | 39.916 | 19.958 | 20 | 20 | -0.042008 | 7.7481
1824 | 30.4 | 2.0016 | 10.4051 | 2 | 10.4 | 39.9149 | 0 | -0.0050535 | 128.0293 | 2.7399e-05 | -0.015161 | 6.4015 | 8.2197e-05 | 6.3864 |  | 10.3864 | 4 | 10.3864 | 39.9149 | 19.9575 | 20 | 20 | -0.042538 | 7.7055
1825 | 30.4167 | 2.0016 | 10.405 | 2 | 10.4 | 39.9139 | 0 | -0.0050258 | 128.0243 | 2.7744e-05 | -0.015077 | 6.4012 | 8.3233e-05 | 6.3862 |  | 10.3862 | 4 | 10.3862 | 39.9139 | 19.9569 | 20 | 20 | -0.04306 | 7.6625
1826 | 30.4333 | 2.0016 | 10.405 | 2 | 10.4 | 39.9129 | 0 | -0.0049977 | 128.0193 | 2.8085e-05 | -0.014993 | 6.401 | 8.4254e-05 | 6.3861 |  | 10.3861 | 4 | 10.3861 | 39.9129 | 19.9564 | 20 | 20 | -0.043574 | 7.6189
1827 | 30.45 | 2.0016 | 10.405 | 2 | 10.4 | 39.9118 | 0 | -0.0049693 | 128.0143 | 2.842e-05 | -0.014908 | 6.4007 | 8.5261e-05 | 6.3859 |  | 10.3859 | 4 | 10.3859 | 39.9118 | 19.9559 | 20 | 20 | -0.044081 | 7.5748
1828 | 30.4667 | 2.0015 | 10.4049 | 2 | 10.4 | 39.9108 | 0 | -0.0049405 | 128.0094 | 2.8751e-05 | -0.014822 | 6.4005 | 8.6253e-05 | 6.3857 |  | 10.3857 | 4 | 10.3857 | 39.9108 | 19.9554 | 20 | 20 | -0.04458 | 7.5302
1829 | 30.4833 | 2.0015 | 10.4049 | 2 | 10.4 | 39.9099 | 0 | -0.0049114 | 128.0045 | 2.9077e-05 | -0.014734 | 6.4002 | 8.723e-05 | 6.3856 |  | 10.3856 | 4 | 10.3856 | 39.9099 | 19.9549 | 20 | 20 | -0.045072 | 7.4852
1830 | 30.5 | 2.0015 | 10.4049 | 2 | 10.4 | 39.9089 | 0 | -0.004882 | 127.9996 | 2.9397e-05 | -0.014646 | 6.4 | 8.8192e-05 | 6.3854 |  | 10.3854 | 4 | 10.3854 | 39.9089 | 19.9544 | 20 | 20 | -0.045556 | 7.4396
1831 | 30.5167 | 2.0015 | 10.4049 | 2 | 10.4 | 39.9079 | 0 | -0.0048523 | 127.9947 | 2.9713e-05 | -0.014557 | 6.3997 | 8.9139e-05 | 6.3853 |  | 10.3853 | 4 | 10.3853 | 39.9079 | 19.954 | 20 | 20 | -0.046033 | 7.3936
1832 | 30.5333 | 2.0015 | 10.4048 | 2 | 10.4 | 39.907 | 0 | -0.0048223 | 127.9899 | 3.0024e-05 | -0.014467 | 6.3995 | 9.0072e-05 | 6.3851 |  | 10.3851 | 4 | 10.3851 | 39.907 | 19.9535 | 20 | 20 | -0.046502 | 7.3471
1833 | 30.55 | 2.0015 | 10.4048 | 2 | 10.4 | 39.9061 | 0 | -0.004792 | 127.9851 | 3.033e-05 | -0.014376 | 6.3993 | 9.099e-05 | 6.385 |  | 10.385 | 4 | 10.385 | 39.9061 | 19.953 | 20 | 20 | -0.046964 | 7.3001
1834 | 30.5667 | 2.0015 | 10.4048 | 2 | 10.4 | 39.9052 | 0 | -0.0047613 | 127.9804 | 3.0631e-05 | -0.014284 | 6.399 | 9.1893e-05 | 6.3848 |  | 10.3848 | 4 | 10.3848 | 39.9052 | 19.9526 | 20 | 20 | -0.047418 | 7.2527
1835 | 30.5833 | 2.0015 | 10.4047 | 2 | 10.4 | 39.9043 | 0 | -0.0047304 | 127.9756 | 3.0927e-05 | -0.014191 | 6.3988 | 9.2781e-05 | 6.3847 |  | 10.3847 | 4 | 10.3847 | 39.9043 | 19.9521 | 20 | 20 | -0.047864 | 7.2048
1836 | 30.6 | 2.0015 | 10.4047 | 2 | 10.4 | 39.9034 | 0 | -0.0046992 | 127.9709 | 3.1218e-05 | -0.014098 | 6.3985 | 9.3655e-05 | 6.3845 |  | 10.3845 | 4 | 10.3845 | 39.9034 | 19.9517 | 20 | 20 | -0.048303 | 7.1565
1837 | 30.6167 | 2.0015 | 10.4047 | 2 | 10.4 | 39.9025 | 0 | -0.0046677 | 127.9663 | 3.1505e-05 | -0.014003 | 6.3983 | 9.4514e-05 | 6.3844 |  | 10.3844 | 4 | 10.3844 | 39.9025 | 19.9513 | 20 | 20 | -0.048734 | 7.1078
1838 | 30.6333 | 2.0014 | 10.4046 | 2 | 10.4 | 39.9017 | 0 | -0.0046359 | 127.9616 | 3.1786e-05 | -0.013908 | 6.3981 | 9.5357e-05 | 6.3843 |  | 10.3843 | 4 | 10.3843 | 39.9017 | 19.9508 | 20 | 20 | -0.049158 | 7.0586
1839 | 30.65 | 2.0014 | 10.4046 | 2 | 10.4 | 39.9009 | 0 | -0.0046039 | 127.957 | 3.2062e-05 | -0.013812 | 6.3979 | 9.6187e-05 | 6.3841 |  | 10.3841 | 4 | 10.3841 | 39.9009 | 19.9504 | 20 | 20 | -0.049574 | 7.0091
1840 | 30.6667 | 2.0014 | 10.4046 | 2 | 10.4 | 39.9 | 0 | -0.0045715 | 127.9525 | 3.2334e-05 | -0.013715 | 6.3976 | 9.7001e-05 | 6.384 |  | 10.384 | 4 | 10.384 | 39.9 | 19.95 | 20 | 20 | -0.049983 | 6.9591
1841 | 30.6833 | 2.0014 | 10.4045 | 2 | 10.4 | 39.8992 | 0 | -0.0045389 | 127.9479 | 3.26e-05 | -0.013617 | 6.3974 | 9.78e-05 | 6.3839 |  | 10.3839 | 4 | 10.3839 | 39.8992 | 19.9496 | 20 | 20 | -0.050384 | 6.9087
1842 | 30.7 | 2.0014 | 10.4045 | 2 | 10.4 | 39.8984 | 0 | -0.0045061 | 127.9434 | 3.2862e-05 | -0.013518 | 6.3972 | 9.8585e-05 | 6.3838 |  | 10.3838 | 4 | 10.3838 | 39.8984 | 19.9492 | 20 | 20 | -0.050777 | 6.8579
1843 | 30.7167 | 2.0014 | 10.4045 | 2 | 10.4 | 39.8977 | 0 | -0.0044729 | 127.9389 | 3.3118e-05 | -0.013419 | 6.3969 | 9.9355e-05 | 6.3836 |  | 10.3836 | 4 | 10.3836 | 39.8977 | 19.9488 | 20 | 20 | -0.051163 | 6.8068
1844 | 30.7333 | 2.0014 | 10.4044 | 2 | 10.4 | 39.8969 | 0 | -0.0044396 | 127.9345 | 3.337e-05 | -0.013319 | 6.3967 | 0.00010011 | 6.3835 |  | 10.3835 | 4 | 10.3835 | 39.8969 | 19.9485 | 20 | 20 | -0.051542 | 6.7552
1845 | 30.75 | 2.0014 | 10.4044 | 2 | 10.4 | 39.8962 | 0 | -0.0044059 | 127.9301 | 3.3617e-05 | -0.013218 | 6.3965 | 0.00010085 | 6.3834 |  | 10.3834 | 4 | 10.3834 | 39.8962 | 19.9481 | 20 | 20 | -0.051913 | 6.7033
1846 | 30.7667 | 2.0014 | 10.4044 | 2 | 10.4 | 39.8954 | 0 | -0.0043721 | 127.9257 | 3.3859e-05 | -0.013116 | 6.3963 | 0.00010158 | 6.3833 |  | 10.3833 | 4 | 10.3833 | 39.8954 | 19.9477 | 20 | 20 | -0.052276 | 6.651
1847 | 30.7833 | 2.0014 | 10.4043 | 2 | 10.4 | 39.8947 | 0 | -0.004338 | 127.9214 | 3.4096e-05 | -0.013014 | 6.3961 | 0.00010229 | 6.3832 |  | 10.3832 | 4 | 10.3832 | 39.8947 | 19.9474 | 20 | 20 | -0.052632 | 6.5984
1848 | 30.8 | 2.0013 | 10.4043 | 2 | 10.4 | 39.894 | 0 | -0.0043037 | 127.9171 | 3.4328e-05 | -0.012911 | 6.3959 | 0.00010298 | 6.383 |  | 10.383 | 4 | 10.383 | 39.894 | 19.947 | 20 | 20 | -0.052981 | 6.5454
1849 | 30.8167 | 2.0013 | 10.4043 | 2 | 10.4 | 39.8934 | 0 | -0.0042691 | 127.9128 | 3.4555e-05 | -0.012807 | 6.3956 | 0.00010367 | 6.3829 |  | 10.3829 | 4 | 10.3829 | 39.8934 | 19.9467 | 20 | 20 | -0.053321 | 6.4921
1850 | 30.8333 | 2.0013 | 10.4042 | 2 | 10.4 | 39.8927 | 0 | -0.0042343 | 127.9086 | 3.4778e-05 | -0.012703 | 6.3954 | 0.00010433 | 6.3828 |  | 10.3828 | 4 | 10.3828 | 39.8927 | 19.9463 | 20 | 20 | -0.053655 | 6.4384
1851 | 30.85 | 2.0013 | 10.4042 | 2 | 10.4 | 39.892 | 0 | -0.0041993 | 127.9044 | 3.4995e-05 | -0.012598 | 6.3952 | 0.00010499 | 6.3827 |  | 10.3827 | 4 | 10.3827 | 39.892 | 19.946 | 20 | 20 | -0.053981 | 6.3845
1852 | 30.8667 | 2.0013 | 10.4042 | 2 | 10.4 | 39.8914 | 0 | -0.0041641 | 127.9002 | 3.5208e-05 | -0.012492 | 6.395 | 0.00010562 | 6.3826 |  | 10.3826 | 4 | 10.3826 | 39.8914 | 19.9457 | 20 | 20 | -0.0543 | 6.3302
1853 | 30.8833 | 2.0013 | 10.4041 | 2 | 10.4 | 39.8908 | 0 | -0.0041287 | 127.8961 | 3.5416e-05 | -0.012386 | 6.3948 | 0.00010625 | 6.3825 |  | 10.3825 | 4 | 10.3825 | 39.8908 | 19.9454 | 20 | 20 | -0.054611 | 6.2755
1854 | 30.9 | 2.0013 | 10.4041 | 2 | 10.4 | 39.8902 | 0 | -0.0040931 | 127.892 | 3.5619e-05 | -0.012279 | 6.3946 | 0.00010686 | 6.3824 |  | 10.3824 | 4 | 10.3824 | 39.8902 | 19.9451 | 20 | 20 | -0.054914 | 6.2206
1855 | 30.9167 | 2.0013 | 10.4041 | 2 | 10.4 | 39.8896 | 0 | -0.0040573 | 127.8879 | 3.5817e-05 | -0.012172 | 6.3944 | 0.00010745 | 6.3823 |  | 10.3823 | 4 | 10.3823 | 39.8896 | 19.9448 | 20 | 20 | -0.055211 | 6.1654
1856 | 30.9333 | 2.0013 | 10.404 | 2 | 10.4 | 39.889 | 0 | -0.0040213 | 127.8839 | 3.601e-05 | -0.012064 | 6.3942 | 0.00010803 | 6.3822 |  | 10.3822 | 4 | 10.3822 | 39.889 | 19.9445 | 20 | 20 | -0.0555 | 6.1099
1857 | 30.95 | 2.0012 | 10.404 | 2 | 10.4 | 39.8884 | 0 | -0.0039851 | 127.8799 | 3.6198e-05 | -0.011955 | 6.394 | 0.0001086 | 6.3822 |  | 10.3822 | 4 | 10.3822 | 39.8884 | 19.9442 | 20 | 20 | -0.055781 | 6.0541
1858 | 30.9667 | 2.0012 | 10.4039 | 2 | 10.4 | 39.8879 | 0 | -0.0039487 | 127.876 | 3.6382e-05 | -0.011846 | 6.3938 | 0.00010915 | 6.3821 |  | 10.3821 | 4 | 10.3821 | 39.8879 | 19.9439 | 20 | 20 | -0.056055 | 5.9981
1859 | 30.9833 | 2.0012 | 10.4039 | 2 | 10.4 | 39.8874 | 0 | -0.0039121 | 127.8721 | 3.6561e-05 | -0.011736 | 6.3936 | 0.00010968 | 6.382 |  | 10.382 | 4 | 10.382 | 39.8874 | 19.9437 | 20 | 20 | -0.056322 | 5.9418
1860 | 31 | 2.0012 | 10.4039 | 2 | 10.4 | 39.8868 | 0 | -0.0038754 | 127.8682 | 3.6735e-05 | -0.011626 | 6.3934 | 0.0001102 | 6.3819 |  | 10.3819 | 4 | 10.3819 | 39.8868 | 19.9434 | 20 | 20 | -0.056582 | 5.8852
1861 | 31.0167 | 2.0012 | 10.4038 | 2 | 10.4 | 39.8863 | 0 | -0.0038385 | 127.8644 | 3.6904e-05 | -0.011515 | 6.3932 | 0.00011071 | 6.3818 |  | 10.3818 | 4 | 10.3818 | 39.8863 | 19.9432 | 20 | 20 | -0.056834 | 5.8283
1862 | 31.0333 | 2.0012 | 10.4038 | 2 | 10.4 | 39.8858 | 0 | -0.0038014 | 127.8606 | 3.7069e-05 | -0.011404 | 6.393 | 0.00011121 | 6.3817 |  | 10.3817 | 4 | 10.3817 | 39.8858 | 19.9429 | 20 | 20 | -0.057079 | 5.7713
1863 | 31.05 | 2.0012 | 10.4038 | 2 | 10.4 | 39.8854 | 0 | -0.0037642 | 127.8568 | 3.7228e-05 | -0.011293 | 6.3928 | 0.00011169 | 6.3817 |  | 10.3817 | 4 | 10.3817 | 39.8854 | 19.9427 | 20 | 20 | -0.057316 | 5.714
1864 | 31.0667 | 2.0012 | 10.4037 | 2 | 10.4 | 39.8849 | 0 | -0.0037268 | 127.8531 | 3.7383e-05 | -0.01118 | 6.3927 | 0.00011215 | 6.3816 |  | 10.3816 | 4 | 10.3816 | 39.8849 | 19.9425 | 20 | 20 | -0.057547 | 5.6564
1865 | 31.0833 | 2.0012 | 10.4037 | 2 | 10.4 | 39.8845 | 0 | -0.0036893 | 127.8494 | 3.7534e-05 | -0.011068 | 6.3925 | 0.0001126 | 6.3815 |  | 10.3815 | 4 | 10.3815 | 39.8845 | 19.9422 | 20 | 20 | -0.05777 | 5.5986
1866 | 31.1 | 2.0011 | 10.4037 | 2 | 10.4 | 39.884 | 0 | -0.0036516 | 127.8457 | 3.7679e-05 | -0.010955 | 6.3923 | 0.00011304 | 6.3814 |  | 10.3814 | 4 | 10.3814 | 39.884 | 19.942 | 20 | 20 | -0.057986 | 5.5406
1867 | 31.1167 | 2.0011 | 10.4036 | 2 | 10.4 | 39.8836 | 0 | -0.0036138 | 127.8421 | 3.782e-05 | -0.010841 | 6.3921 | 0.00011346 | 6.3814 |  | 10.3814 | 4 | 10.3814 | 39.8836 | 19.9418 | 20 | 20 | -0.058195 | 5.4825
1868 | 31.1333 | 2.0011 | 10.4036 | 2 | 10.4 | 39.8832 | 0 | -0.0035758 | 127.8385 | 3.7956e-05 | -0.010727 | 6.3919 | 0.00011387 | 6.3813 |  | 10.3813 | 4 | 10.3813 | 39.8832 | 19.9416 | 20 | 20 | -0.058396 | 5.4241
1869 | 31.15 | 2.0011 | 10.4035 | 2 | 10.4 | 39.8828 | 0 | -0.0035377 | 127.835 | 3.8088e-05 | -0.010613 | 6.3917 | 0.00011426 | 6.3813 |  | 10.3813 | 4 | 10.3813 | 39.8828 | 19.9414 | 20 | 20 | -0.058591 | 5.3655
1870 | 31.1667 | 2.0011 | 10.4035 | 2 | 10.4 | 39.8824 | 0 | -0.0034995 | 127.8315 | 3.8215e-05 | -0.010499 | 6.3916 | 0.00011464 | 6.3812 |  | 10.3812 | 4 | 10.3812 | 39.8824 | 19.9412 | 20 | 20 | -0.058778 | 5.3067
1871 | 31.1833 | 2.0011 | 10.4035 | 2 | 10.4 | 39.8821 | 0 | -0.0034612 | 127.828 | 3.8337e-05 | -0.010384 | 6.3914 | 0.00011501 | 6.3811 |  | 10.3811 | 4 | 10.3811 | 39.8821 | 19.941 | 20 | 20 | -0.058958 | 5.2477
1872 | 31.2 | 2.0011 | 10.4034 | 2 | 10.4 | 39.8817 | 0 | -0.0034227 | 127.8246 | 3.8454e-05 | -0.010268 | 6.3912 | 0.00011536 | 6.3811 |  | 10.3811 | 4 | 10.3811 | 39.8817 | 19.9409 | 20 | 20 | -0.059132 | 5.1886
1873 | 31.2167 | 2.0011 | 10.4034 | 2 | 10.4 | 39.8814 | 0 | -0.0033842 | 127.8212 | 3.8567e-05 | -0.010152 | 6.3911 | 0.0001157 | 6.381 |  | 10.381 | 4 | 10.381 | 39.8814 | 19.9407 | 20 | 20 | -0.059298 | 5.1293
1874 | 31.2333 | 2.001 | 10.4033 | 2 | 10.4 | 39.8811 | 0 | -0.0033455 | 127.8179 | 3.8676e-05 | -0.010036 | 6.3909 | 0.00011603 | 6.381 |  | 10.381 | 4 | 10.381 | 39.8811 | 19.9405 | 20 | 20 | -0.059457 | 5.0698
1875 | 31.25 | 2.001 | 10.4033 | 2 | 10.4 | 39.8808 | 0 | -0.0033067 | 127.8146 | 3.878e-05 | -0.0099201 | 6.3907 | 0.00011634 | 6.3809 |  | 10.3809 | 4 | 10.3809 | 39.8808 | 19.9404 | 20 | 20 | -0.059609 | 5.0102
1876 | 31.2667 | 2.001 | 10.4033 | 2 | 10.4 | 39.8805 | 0 | -0.0032678 | 127.8113 | 3.8879e-05 | -0.0098035 | 6.3906 | 0.00011664 | 6.3809 |  | 10.3809 | 4 | 10.3809 | 39.8805 | 19.9402 | 20 | 20 | -0.059754 | 4.9505
1877 | 31.2833 | 2.001 | 10.4032 | 2 | 10.4 | 39.8802 | 0 | -0.0032288 | 127.8081 | 3.8973e-05 | -0.0096865 | 6.3904 | 0.00011692 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.8802 | 19.9401 | 20 | 20 | -0.059892 | 4.8906
1878 | 31.3 | 2.001 | 10.4032 | 2 | 10.4 | 39.88 | 0 | -0.0031898 | 127.8049 | 3.9064e-05 | -0.0095694 | 6.3902 | 0.00011719 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.88 | 19.94 | 20 | 20 | -0.060024 | 4.8306
1879 | 31.3167 | 2.001 | 10.4032 | 2 | 10.4 | 39.8797 | 0 | -0.0031506 | 127.8017 | 3.9149e-05 | -0.0094519 | 6.3901 | 0.00011745 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.8797 | 19.9399 | 20 | 20 | -0.060148 | 4.7704
1880 | 31.3333 | 2.001 | 10.4031 | 2 | 10.4 | 39.8795 | 0 | -0.0031114 | 127.7986 | 3.923e-05 | -0.0093342 | 6.3899 | 0.00011769 | 6.3807 |  | 10.3807 | 4 | 10.3807 | 39.8795 | 19.9397 | 20 | 20 | -0.060266 | 4.7102
1881 | 31.35 | 2.001 | 10.4031 | 2 | 10.4 | 39.8792 | 0 | -0.0030721 | 127.7956 | 3.9307e-05 | -0.0092163 | 6.3898 | 0.00011792 | 6.3807 |  | 10.3807 | 4 | 10.3807 | 39.8792 | 19.9396 | 20 | 20 | -0.060377 | 4.6498
1882 | 31.3667 | 2.0009 | 10.403 | 2 | 10.4 | 39.879 | 0 | -0.0030327 | 127.7925 | 3.9379e-05 | -0.0090982 | 6.3896 | 0.00011814 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.879 | 19.9395 | 20 | 20 | -0.060481 | 4.5893
1883 | 31.3833 | 2.0009 | 10.403 | 2 | 10.4 | 39.8788 | 0 | -0.0029933 | 127.7895 | 3.9447e-05 | -0.0089798 | 6.3895 | 0.00011834 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8788 | 19.9394 | 20 | 20 | -0.060578 | 4.5287
1884 | 31.4 | 2.0009 | 10.403 | 2 | 10.4 | 39.8787 | 0 | -0.0029538 | 127.7866 | 3.9511e-05 | -0.0088613 | 6.3893 | 0.00011853 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8787 | 19.9393 | 20 | 20 | -0.060668 | 4.468
1885 | 31.4167 | 2.0009 | 10.4029 | 2 | 10.4 | 39.8785 | 0 | -0.0029142 | 127.7837 | 3.957e-05 | -0.0087426 | 6.3892 | 0.00011871 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8785 | 19.9392 | 20 | 20 | -0.060752 | 4.4073
1886 | 31.4333 | 2.0009 | 10.4029 | 2 | 10.4 | 39.8783 | 0 | -0.0028746 | 127.7808 | 3.9624e-05 | -0.0086237 | 6.389 | 0.00011887 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8783 | 19.9392 | 20 | 20 | -0.060829 | 4.3465
1887 | 31.45 | 2.0009 | 10.4028 | 2 | 10.4 | 39.8782 | 0 | -0.0028349 | 127.778 | 3.9675e-05 | -0.0085047 | 6.3889 | 0.00011902 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8782 | 19.9391 | 20 | 20 | -0.0609 | 4.2856
1888 | 31.4667 | 2.0009 | 10.4028 | 2 | 10.4 | 39.8781 | 0 | -0.0027952 | 127.7752 | 3.9721e-05 | -0.0083855 | 6.3888 | 0.00011916 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8781 | 19.939 | 20 | 20 | -0.060964 | 4.2246
1889 | 31.4833 | 2.0009 | 10.4028 | 2 | 10.4 | 39.878 | 0 | -0.0027554 | 127.7724 | 3.9762e-05 | -0.0082662 | 6.3886 | 0.00011929 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.878 | 19.939 | 20 | 20 | -0.061021 | 4.1636
1890 | 31.5 | 2.0008 | 10.4027 | 2 | 10.4 | 39.8779 | 0 | -0.0027156 | 127.7697 | 3.98e-05 | -0.0081468 | 6.3885 | 0.0001194 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8779 | 19.9389 | 20 | 20 | -0.061072 | 4.1025
1891 | 31.5167 | 2.0008 | 10.4027 | 2 | 10.4 | 39.8778 | 0 | -0.0026758 | 127.767 | 3.9833e-05 | -0.0080273 | 6.3884 | 0.0001195 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8778 | 19.9389 | 20 | 20 | -0.061116 | 4.0414
1892 | 31.5333 | 2.0008 | 10.4026 | 2 | 10.4 | 39.8777 | 0 | -0.0026359 | 127.7644 | 3.9862e-05 | -0.0079077 | 6.3882 | 0.00011959 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8777 | 19.9388 | 20 | 20 | -0.061154 | 3.9802
1893 | 31.55 | 2.0008 | 10.4026 | 2 | 10.4 | 39.8776 | 0 | -0.002596 | 127.7618 | 3.9887e-05 | -0.0077881 | 6.3881 | 0.00011966 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8776 | 19.9388 | 20 | 20 | -0.061186 | 3.9191
1894 | 31.5667 | 2.0008 | 10.4026 | 2 | 10.4 | 39.8776 | 0 | -0.0025561 | 127.7592 | 3.9907e-05 | -0.0076684 | 6.388 | 0.00011972 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8776 | 19.9388 | 20 | 20 | -0.061211 | 3.8578
1895 | 31.5833 | 2.0008 | 10.4025 | 2 | 10.4 | 39.8775 | 0 | -0.0025162 | 127.7567 | 3.9923e-05 | -0.0075486 | 6.3878 | 0.00011977 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.06123 | 3.7966
1896 | 31.6 | 2.0008 | 10.4025 | 2 | 10.4 | 39.8775 | 0 | -0.0024763 | 127.7542 | 3.9936e-05 | -0.0074288 | 6.3877 | 0.00011981 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.061242 | 3.7354
1897 | 31.6167 | 2.0008 | 10.4024 | 2 | 10.4 | 39.8775 | 0 | -0.0024363 | 127.7518 | 3.9944e-05 | -0.007309 | 6.3876 | 0.00011983 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.061248 | 3.6741
1898 | 31.6333 | 2.0007 | 10.4024 | 2 | 10.4 | 39.8775 | 0 | -0.0023964 | 127.7494 | 3.9948e-05 | -0.0071891 | 6.3875 | 0.00011984 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.061248 | 3.6129
1899 | 31.65 | 2.0007 | 10.4024 | 2 | 10.4 | 39.8775 | 0 | -0.0023564 | 127.747 | 3.9948e-05 | -0.0070693 | 6.3874 | 0.00011984 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.061242 | 3.5516
1900 | 31.6667 | 2.0007 | 10.4023 | 2 | 10.4 | 39.8775 | 0 | -0.0023165 | 127.7447 | 3.9944e-05 | -0.0069494 | 6.3872 | 0.00011983 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8775 | 19.9388 | 20 | 20 | -0.061229 | 3.4904
1901 | 31.6833 | 2.0007 | 10.4023 | 2 | 10.4 | 39.8776 | 0 | -0.0022765 | 127.7424 | 3.9935e-05 | -0.0068296 | 6.3871 | 0.00011981 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8776 | 19.9388 | 20 | 20 | -0.061211 | 3.4292
1902 | 31.7 | 2.0007 | 10.4022 | 2 | 10.4 | 39.8776 | 0 | -0.0022366 | 127.7402 | 3.9923e-05 | -0.0067099 | 6.387 | 0.00011977 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8776 | 19.9388 | 20 | 20 | -0.061186 | 3.368
1903 | 31.7167 | 2.0007 | 10.4022 | 2 | 10.4 | 39.8777 | 0 | -0.0021967 | 127.738 | 3.9907e-05 | -0.0065901 | 6.3869 | 0.00011972 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8777 | 19.9388 | 20 | 20 | -0.061155 | 3.3069
1904 | 31.7333 | 2.0007 | 10.4022 | 2 | 10.4 | 39.8778 | 0 | -0.0021568 | 127.7359 | 3.9887e-05 | -0.0064705 | 6.3868 | 0.00011966 | 6.3804 |  | 10.3804 | 4 | 10.3804 | 39.8778 | 19.9389 | 20 | 20 | -0.061118 | 3.2457
1905 | 31.75 | 2.0007 | 10.4021 | 2 | 10.4 | 39.8778 | 0 | -0.002117 | 127.7337 | 3.9863e-05 | -0.0063509 | 6.3867 | 0.00011959 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8778 | 19.9389 | 20 | 20 | -0.061076 | 3.1847
1906 | 31.7667 | 2.0006 | 10.4021 | 2 | 10.4 | 39.8779 | 0 | -0.0020771 | 127.7317 | 3.9835e-05 | -0.0062314 | 6.3866 | 0.00011951 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8779 | 19.939 | 20 | 20 | -0.061027 | 3.1236
1907 | 31.7833 | 2.0006 | 10.402 | 2 | 10.4 | 39.8781 | 0 | -0.0020373 | 127.7296 | 3.9804e-05 | -0.006112 | 6.3865 | 0.00011941 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8781 | 19.939 | 20 | 20 | -0.060972 | 3.0627
1908 | 31.8 | 2.0006 | 10.402 | 2 | 10.4 | 39.8782 | 0 | -0.0019976 | 127.7276 | 3.9768e-05 | -0.0059927 | 6.3864 | 0.0001193 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8782 | 19.9391 | 20 | 20 | -0.060912 | 3.0017
1909 | 31.8167 | 2.0006 | 10.402 | 2 | 10.4 | 39.8783 | 0 | -0.0019578 | 127.7257 | 3.9729e-05 | -0.0058735 | 6.3863 | 0.00011919 | 6.3805 |  | 10.3805 | 4 | 10.3805 | 39.8783 | 19.9392 | 20 | 20 | -0.060846 | 2.9409
1910 | 31.8333 | 2.0006 | 10.4019 | 2 | 10.4 | 39.8785 | 0 | -0.0019181 | 127.7238 | 3.9685e-05 | -0.0057544 | 6.3862 | 0.00011906 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8785 | 19.9392 | 20 | 20 | -0.060774 | 2.8801
1911 | 31.85 | 2.0006 | 10.4019 | 2 | 10.4 | 39.8786 | 0 | -0.0018785 | 127.7219 | 3.9639e-05 | -0.0056355 | 6.3861 | 0.00011892 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8786 | 19.9393 | 20 | 20 | -0.060696 | 2.8194
1912 | 31.8667 | 2.0006 | 10.4018 | 2 | 10.4 | 39.8788 | 0 | -0.0018389 | 127.72 | 3.9588e-05 | -0.0055167 | 6.386 | 0.00011876 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.8788 | 19.9394 | 20 | 20 | -0.060613 | 2.7588
1913 | 31.8833 | 2.0006 | 10.4018 | 2 | 10.4 | 39.879 | 0 | -0.0017994 | 127.7182 | 3.9534e-05 | -0.0053981 | 6.3859 | 0.0001186 | 6.3806 |  | 10.3806 | 4 | 10.3806 | 39.879 | 19.9395 | 20 | 20 | -0.060524 | 2.6983
1914 | 31.9 | 2.0005 | 10.4018 | 2 | 10.4 | 39.8791 | 0 | -0.0017599 | 127.7165 | 3.9476e-05 | -0.0052797 | 6.3858 | 0.00011843 | 6.3807 |  | 10.3807 | 4 | 10.3807 | 39.8791 | 19.9396 | 20 | 20 | -0.060429 | 2.6379
1915 | 31.9167 | 2.0005 | 10.4017 | 2 | 10.4 | 39.8793 | 0 | -0.0017205 | 127.7148 | 3.9414e-05 | -0.0051615 | 6.3857 | 0.00011824 | 6.3807 |  | 10.3807 | 4 | 10.3807 | 39.8793 | 19.9397 | 20 | 20 | -0.060329 | 2.5775
1916 | 31.9333 | 2.0005 | 10.4017 | 2 | 10.4 | 39.8796 | 0 | -0.0016811 | 127.7131 | 3.9349e-05 | -0.0050434 | 6.3857 | 0.00011805 | 6.3807 |  | 10.3807 | 4 | 10.3807 | 39.8796 | 19.9398 | 20 | 20 | -0.060224 | 2.5173
1917 | 31.95 | 2.0005 | 10.4016 | 2 | 10.4 | 39.8798 | 0 | -0.0016419 | 127.7114 | 3.928e-05 | -0.0049256 | 6.3856 | 0.00011784 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.8798 | 19.9399 | 20 | 20 | -0.060113 | 2.4572
1918 | 31.9667 | 2.0005 | 10.4016 | 2 | 10.4 | 39.88 | 0 | -0.0016027 | 127.7098 | 3.9207e-05 | -0.004808 | 6.3855 | 0.00011762 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.88 | 19.94 | 20 | 20 | -0.059996 | 2.3972
1919 | 31.9833 | 2.0005 | 10.4016 | 2 | 10.4 | 39.8803 | 0 | -0.0015635 | 127.7083 | 3.9131e-05 | -0.0046906 | 6.3854 | 0.00011739 | 6.3808 |  | 10.3808 | 4 | 10.3808 | 39.8803 | 19.9401 | 20 | 20 | -0.059874 | 2.3373
1920 | 32 | 2.0005 | 10.4015 | 2 | 10.4 | 39.8805 | 0 | -0.0015245 | 127.7067 | 3.9052e-05 | -0.0045734 | 6.3853 | 0.00011716 | 6.3809 |  | 10.3809 | 4 | 10.3809 | 39.8805 | 19.9403 | 20 | 20 | -0.059747 | 2.2776
1921 | 32.0167 | 2.0005 | 10.4015 | 2 | 10.4 | 39.8808 | 0 | -0.0014855 | 127.7053 | 3.8969e-05 | -0.0044565 | 6.3853 | 0.00011691 | 6.3809 |  | 10.3809 | 4 | 10.3809 | 39.8808 | 19.9404 | 20 | 20 | -0.059615 | 2.218
1922 | 32.0333 | 2.0005 | 10.4014 | 2 | 10.4 | 39.881 | 0 | -0.0014466 | 127.7038 | 3.8883e-05 | -0.0043399 | 6.3852 | 0.00011665 | 6.381 |  | 10.381 | 4 | 10.381 | 39.881 | 19.9405 | 20 | 20 | -0.059477 | 2.1585
1923 | 32.05 | 2.0004 | 10.4014 | 2 | 10.4 | 39.8813 | 0 | -0.0014078 | 127.7024 | 3.8793e-05 | -0.0042235 | 6.3851 | 0.00011638 | 6.381 |  | 10.381 | 4 | 10.381 | 39.8813 | 19.9407 | 20 | 20 | -0.059334 | 2.0992
1924 | 32.0667 | 2.0004 | 10.4014 | 2 | 10.4 | 39.8816 | 0 | -0.0013691 | 127.701 | 3.87e-05 | -0.0041074 | 6.3851 | 0.0001161 | 6.3811 |  | 10.3811 | 4 | 10.3811 | 39.8816 | 19.9408 | 20 | 20 | -0.059186 | 2.04
1925 | 32.0833 | 2.0004 | 10.4013 | 2 | 10.4 | 39.8819 | 0 | -0.0013305 | 127.6997 | 3.8603e-05 | -0.0039916 | 6.385 | 0.00011581 | 6.3811 |  | 10.3811 | 4 | 10.3811 | 39.8819 | 19.941 | 20 | 20 | -0.059033 | 1.9809
1926 | 32.1 | 2.0004 | 10.4013 | 2 | 10.4 | 39.8823 | 0 | -0.001292 | 127.6984 | 3.8503e-05 | -0.0038761 | 6.3849 | 0.00011551 | 6.3812 |  | 10.3812 | 4 | 10.3812 | 39.8823 | 19.9411 | 20 | 20 | -0.058875 | 1.9221
1927 | 32.1167 | 2.0004 | 10.4013 | 2 | 10.4 | 39.8826 | 0 | -0.0012536 | 127.6972 | 3.84e-05 | -0.0037609 | 6.3849 | 0.0001152 | 6.3812 |  | 10.3812 | 4 | 10.3812 | 39.8826 | 19.9413 | 20 | 20 | -0.058712 | 1.8633
1928 | 32.1333 | 2.0004 | 10.4012 | 2 | 10.4 | 39.8829 | 0 | -0.0012153 | 127.6959 | 3.8294e-05 | -0.003646 | 6.3848 | 0.00011488 | 6.3813 |  | 10.3813 | 4 | 10.3813 | 39.8829 | 19.9415 | 20 | 20 | -0.058544 | 1.8048
1929 | 32.15 | 2.0004 | 10.4012 | 2 | 10.4 | 39.8833 | 0 | -0.0011771 | 127.6948 | 3.8184e-05 | -0.0035314 | 6.3847 | 0.00011455 | 6.3813 |  | 10.3813 | 4 | 10.3813 | 39.8833 | 19.9416 | 20 | 20 | -0.058371 | 1.7464
1930 | 32.1667 | 2.0004 | 10.4011 | 2 | 10.4 | 39.8836 | 0 | -0.0011391 | 127.6936 | 3.8071e-05 | -0.0034172 | 6.3847 | 0.00011421 | 6.3814 |  | 10.3814 | 4 | 10.3814 | 39.8836 | 19.9418 | 20 | 20 | -0.058193 | 1.6882
1931 | 32.1833 | 2.0003 | 10.4011 | 2 | 10.4 | 39.884 | 0 | -0.0011011 | 127.6925 | 3.7955e-05 | -0.0033034 | 6.3846 | 0.00011387 | 6.3814 |  | 10.3814 | 4 | 10.3814 | 39.884 | 19.942 | 20 | 20 | -0.05801 | 1.6302
1932 | 32.2 | 2.0003 | 10.4011 | 2 | 10.4 | 39.8844 | 0 | -0.0010633 | 127.6915 | 3.7836e-05 | -0.0031899 | 6.3846 | 0.00011351 | 6.3815 |  | 10.3815 | 4 | 10.3815 | 39.8844 | 19.9422 | 20 | 20 | -0.057823 | 1.5724
1933 | 32.2167 | 2.0003 | 10.401 | 2 | 10.4 | 39.8847 | 0 | -0.0010256 | 127.6904 | 3.7714e-05 | -0.0030767 | 6.3845 | 0.00011314 | 6.3816 |  | 10.3816 | 4 | 10.3816 | 39.8847 | 19.9424 | 20 | 20 | -0.05763 | 1.5148
1934 | 32.2333 | 2.0003 | 10.401 | 2 | 10.4 | 39.8851 | 0 | -0.00098798 | 127.6894 | 3.7588e-05 | -0.0029639 | 6.3845 | 0.00011276 | 6.3816 |  | 10.3816 | 4 | 10.3816 | 39.8851 | 19.9426 | 20 | 20 | -0.057434 | 1.4573
1935 | 32.25 | 2.0003 | 10.401 | 2 | 10.4 | 39.8855 | 0 | -0.00095052 | 127.6885 | 3.746e-05 | -0.0028516 | 6.3844 | 0.00011238 | 6.3817 |  | 10.3817 | 4 | 10.3817 | 39.8855 | 19.9428 | 20 | 20 | -0.057232 | 1.4001
1936 | 32.2667 | 2.0003 | 10.4009 | 2 | 10.4 | 39.8859 | 0 | -0.00091319 | 127.6876 | 3.7329e-05 | -0.0027396 | 6.3844 | 0.00011199 | 6.3818 |  | 10.3818 | 4 | 10.3818 | 39.8859 | 19.943 | 20 | 20 | -0.057026 | 1.3431
1937 | 32.2833 | 2.0003 | 10.4009 | 2 | 10.4 | 39.8864 | 0 | -0.000876 | 127.6867 | 3.7194e-05 | -0.002628 | 6.3843 | 0.00011158 | 6.3818 |  | 10.3818 | 4 | 10.3818 | 39.8864 | 19.9432 | 20 | 20 | -0.056816 | 1.2863
1938 | 32.3 | 2.0003 | 10.4008 | 2 | 10.4 | 39.8868 | 0 | -0.00083894 | 127.6859 | 3.7057e-05 | -0.0025168 | 6.3843 | 0.00011117 | 6.3819 |  | 10.3819 | 4 | 10.3819 | 39.8868 | 19.9434 | 20 | 20 | -0.056601 | 1.2297
1939 | 32.3167 | 2.0003 | 10.4008 | 2 | 10.4 | 39.8872 | 0 | -0.00080203 | 127.6851 | 3.6917e-05 | -0.0024061 | 6.3843 | 0.00011075 | 6.382 |  | 10.382 | 4 | 10.382 | 39.8872 | 19.9436 | 20 | 20 | -0.056381 | 1.1733
1940 | 32.3333 | 2.0002 | 10.4008 | 2 | 10.4 | 39.8877 | 0 | -0.00076525 | 127.6843 | 3.6773e-05 | -0.0022958 | 6.3842 | 0.00011032 | 6.382 |  | 10.382 | 4 | 10.382 | 39.8877 | 19.9438 | 20 | 20 | -0.056157 | 1.1171
1941 | 32.35 | 2.0002 | 10.4007 | 2 | 10.4 | 39.8881 | 0 | -0.00072863 | 127.6836 | 3.6627e-05 | -0.0021859 | 6.3842 | 0.00010988 | 6.3821 |  | 10.3821 | 4 | 10.3821 | 39.8881 | 19.9441 | 20 | 20 | -0.055929 | 1.0612
1942 | 32.3667 | 2.0002 | 10.4007 | 2 | 10.4 | 39.8886 | 0 | -0.00069215 | 127.6829 | 3.6479e-05 | -0.0020764 | 6.3841 | 0.00010944 | 6.3822 |  | 10.3822 | 4 | 10.3822 | 39.8886 | 19.9443 | 20 | 20 | -0.055697 | 1.0055
1943 | 32.3833 | 2.0002 | 10.4007 | 2 | 10.4 | 39.8891 | 0 | -0.00065582 | 127.6822 | 3.6327e-05 | -0.0019675 | 6.3841 | 0.00010898 | 6.3823 |  | 10.3823 | 4 | 10.3823 | 39.8891 | 19.9445 | 20 | 20 | -0.05546 | 0.95004
1944 | 32.4 | 2.0002 | 10.4006 | 2 | 10.4 | 39.8896 | 0 | -0.00061965 | 127.6816 | 3.6173e-05 | -0.0018589 | 6.3841 | 0.00010852 | 6.3823 |  | 10.3823 | 4 | 10.3823 | 39.8896 | 19.9448 | 20 | 20 | -0.055219 | 0.89483
1945 | 32.4167 | 2.0002 | 10.4006 | 2 | 10.4 | 39.8901 | 0 | -0.00058363 | 127.681 | 3.6016e-05 | -0.0017509 | 6.3841 | 0.00010805 | 6.3824 |  | 10.3824 | 4 | 10.3824 | 39.8901 | 19.945 | 20 | 20 | -0.054974 | 0.83985
1946 | 32.4333 | 2.0002 | 10.4005 | 2 | 10.4 | 39.8905 | 0 | -0.00054778 | 127.6805 | 3.5856e-05 | -0.0016433 | 6.384 | 0.00010757 | 6.3825 |  | 10.3825 | 4 | 10.3825 | 39.8905 | 19.9453 | 20 | 20 | -0.054725 | 0.78513
1947 | 32.45 | 2.0002 | 10.4005 | 2 | 10.4 | 39.8911 | 0 | -0.00051208 | 127.68 | 3.5693e-05 | -0.0015362 | 6.384 | 0.00010708 | 6.3826 |  | 10.3826 | 4 | 10.3826 | 39.8911 | 19.9455 | 20 | 20 | -0.054472 | 0.73065
1948 | 32.4667 | 2.0001 | 10.4005 | 2 | 10.4 | 39.8916 | 0 | -0.00047655 | 127.6795 | 3.5528e-05 | -0.0014297 | 6.384 | 0.00010658 | 6.3827 |  | 10.3827 | 4 | 10.3827 | 39.8916 | 19.9458 | 20 | 20 | -0.054215 | 0.67644
1949 | 32.4833 | 2.0001 | 10.4004 | 2 | 10.4 | 39.8921 | 0 | -0.00044119 | 127.679 | 3.5361e-05 | -0.0013236 | 6.384 | 0.00010608 | 6.3827 |  | 10.3827 | 4 | 10.3827 | 39.8921 | 19.946 | 20 | 20 | -0.053954 | 0.62249
1950 | 32.5 | 2.0001 | 10.4004 | 2 | 10.4 | 39.8926 | 0 | -0.000406 | 127.6786 | 3.519e-05 | -0.001218 | 6.3839 | 0.00010557 | 6.3828 |  | 10.3828 | 4 | 10.3828 | 39.8926 | 19.9463 | 20 | 20 | -0.053689 | 0.5688
1951 | 32.5167 | 2.0001 | 10.4004 | 2 | 10.4 | 39.8932 | 0 | -0.00037099 | 127.6783 | 3.5018e-05 | -0.001113 | 6.3839 | 0.00010505 | 6.3829 |  | 10.3829 | 4 | 10.3829 | 39.8932 | 19.9466 | 20 | 20 | -0.05342 | 0.51538
1952 | 32.5333 | 2.0001 | 10.4003 | 2 | 10.4 | 39.8937 | 0 | -0.00033614 | 127.6779 | 3.4842e-05 | -0.0010084 | 6.3839 | 0.00010453 | 6.383 |  | 10.383 | 4 | 10.383 | 39.8937 | 19.9469 | 20 | 20 | -0.053148 | 0.46223
1953 | 32.55 | 2.0001 | 10.4003 | 2 | 10.4 | 39.8943 | 0 | -0.00030148 | 127.6776 | 3.4665e-05 | -0.00090444 | 6.3839 | 0.00010399 | 6.3831 |  | 10.3831 | 4 | 10.3831 | 39.8943 | 19.9471 | 20 | 20 | -0.052872 | 0.40936
1954 | 32.5667 | 2.0001 | 10.4003 | 2 | 10.4 | 39.8948 | 0 | -0.00026699 | 127.6774 | 3.4484e-05 | -0.00080098 | 6.3839 | 0.00010345 | 6.3832 |  | 10.3832 | 4 | 10.3832 | 39.8948 | 19.9474 | 20 | 20 | -0.052592 | 0.35677
1955 | 32.5833 | 2.0001 | 10.4002 | 2 | 10.4 | 39.8954 | 0 | -0.00023269 | 127.6771 | 3.4302e-05 | -0.00069808 | 6.3839 | 0.00010291 | 6.3833 |  | 10.3833 | 4 | 10.3833 | 39.8954 | 19.9477 | 20 | 20 | -0.052308 | 0.30446
1956 | 32.6 | 2.0001 | 10.4002 | 2 | 10.4 | 39.896 | 0 | -0.00019858 | 127.6769 | 3.4117e-05 | -0.00059573 | 6.3838 | 0.00010235 | 6.3834 |  | 10.3834 | 4 | 10.3834 | 39.896 | 19.948 | 20 | 20 | -0.052021 | 0.25244
1957 | 32.6167 | 2.0001 | 10.4002 | 2 | 10.4 | 39.8965 | 0 | -0.00016465 | 127.6768 | 3.393e-05 | -0.00049394 | 6.3838 | 0.00010179 | 6.3834 |  | 10.3834 | 4 | 10.3834 | 39.8965 | 19.9483 | 20 | 20 | -0.051731 | 0.20071
1958 | 32.6333 | 2 | 10.4001 | 2 | 10.4 | 39.8971 | 0 | -0.00013091 | 127.6766 | 3.374e-05 | -0.00039272 | 6.3838 | 0.00010122 | 6.3835 |  | 10.3835 | 4 | 10.3835 | 39.8971 | 19.9486 | 20 | 20 | -0.051436 | 0.14927
1959 | 32.65 | 2 | 10.4001 | 2 | 10.4 | 39.8977 | 0 | -9.7357e-05 | 127.6765 | 3.3548e-05 | -0.00029207 | 6.3838 | 0.00010065 | 6.3836 |  | 10.3836 | 4 | 10.3836 | 39.8977 | 19.9489 | 20 | 20 | -0.051139 | 0.09813
1960 | 32.6667 | 2 | 10.4001 | 2 | 10.4 | 39.8983 | 0 | -6.4003e-05 | 127.6765 | 3.3354e-05 | -0.00019201 | 6.3838 | 0.00010006 | 6.3837 |  | 10.3837 | 4 | 10.3837 | 39.8983 | 19.9492 | 20 | 20 | -0.050838 | 0.047291
1961 | 32.6833 | 2 | 10.4 | 2 | 10.4 | 39.8989 | 0 | -3.0845e-05 | 127.6764 | 3.3158e-05 | -9.2535e-05 | 6.3838 | 9.9474e-05 | 6.3838 |  | 10.3838 | 4 | 10.3838 | 39.8989 | 19.9495 | 20 | 20 | -0.050534 | -0.0032424
1962 | 32.7 | 2 | 10.4 | 2 | 10.4 | 39.8995 | 0 | 2.1148e-06 | 127.6764 | 3.296e-05 | 6.3444e-06 | 6.3838 | 9.8879e-05 | 6.3839 |  | 10.3839 | 4 | 10.3839 | 39.8995 | 19.9498 | 20 | 20 | -0.050226 | -0.053469
1963 | 32.7167 | 2 | 10.4 | 2 | 10.4 | 39.9002 | 0 | 3.4874e-05 | 127.6765 | 3.2759e-05 | 0.00010462 | 6.3838 | 9.8277e-05 | 6.384 |  | 10.384 | 4 | 10.384 | 39.9002 | 19.9501 | 20 | 20 | -0.049916 | -0.10338
1964 | 32.7333 | 2 | 10.3999 | 2 | 10.4 | 39.9008 | 0 | 6.743e-05 | 127.6765 | 3.2557e-05 | 0.00020229 | 6.3838 | 9.767e-05 | 6.3841 |  | 10.3841 | 4 | 10.3841 | 39.9008 | 19.9504 | 20 | 20 | -0.049602 | -0.15299
1965 | 32.75 | 2 | 10.3999 | 2 | 10.4 | 39.9014 | 0 | 9.9782e-05 | 127.6766 | 3.2352e-05 | 0.00029935 | 6.3838 | 9.7055e-05 | 6.3842 |  | 10.3842 | 4 | 10.3842 | 39.9014 | 19.9507 | 20 | 20 | -0.049285 | -0.20227
1966 | 32.7667 | 2 | 10.3999 | 2 | 10.4 | 39.9021 | 0 | 0.00013193 | 127.6768 | 3.2145e-05 | 0.00039578 | 6.3838 | 9.6435e-05 | 6.3843 |  | 10.3843 | 4 | 10.3843 | 39.9021 | 19.951 | 20 | 20 | -0.048965 | -0.25124
1967 | 32.7833 | 1.9999 | 10.3998 | 2 | 10.4 | 39.9027 | 0 | 0.00016386 | 127.6769 | 3.1936e-05 | 0.00049159 | 6.3838 | 9.5809e-05 | 6.3844 |  | 10.3844 | 4 | 10.3844 | 39.9027 | 19.9514 | 20 | 20 | -0.048642 | -0.29988
1968 | 32.8 | 1.9999 | 10.3998 | 2 | 10.4 | 39.9034 | 0 | 0.00019559 | 127.6771 | 3.1726e-05 | 0.00058677 | 6.3839 | 9.5177e-05 | 6.3845 |  | 10.3845 | 4 | 10.3845 | 39.9034 | 19.9517 | 20 | 20 | -0.048316 | -0.34819
1969 | 32.8167 | 1.9999 | 10.3998 | 2 | 10.4 | 39.904 | 0 | 0.0002271 | 127.6774 | 3.1513e-05 | 0.00068131 | 6.3839 | 9.4539e-05 | 6.3846 |  | 10.3846 | 4 | 10.3846 | 39.904 | 19.952 | 20 | 20 | -0.047987 | -0.39618
1970 | 32.8333 | 1.9999 | 10.3997 | 2 | 10.4 | 39.9047 | 0 | 0.0002584 | 127.6776 | 3.1298e-05 | 0.0007752 | 6.3839 | 9.3895e-05 | 6.3848 |  | 10.3848 | 4 | 10.3848 | 39.9047 | 19.9523 | 20 | 20 | -0.047655 | -0.44384
1971 | 32.85 | 1.9999 | 10.3997 | 2 | 10.4 | 39.9054 | 0 | 0.00028948 | 127.6779 | 3.1082e-05 | 0.00086845 | 6.3839 | 9.3246e-05 | 6.3849 |  | 10.3849 | 4 | 10.3849 | 39.9054 | 19.9527 | 20 | 20 | -0.047321 | -0.49116
1972 | 32.8667 | 1.9999 | 10.3997 | 2 | 10.4 | 39.906 | 0 | 0.00032035 | 127.6782 | 3.0864e-05 | 0.00096104 | 6.3839 | 9.2591e-05 | 6.385 |  | 10.385 | 4 | 10.385 | 39.906 | 19.953 | 20 | 20 | -0.046983 | -0.53814
1973 | 32.8833 | 1.9999 | 10.3996 | 2 | 10.4 | 39.9067 | 0 | 0.00035099 | 127.6786 | 3.0644e-05 | 0.001053 | 6.3839 | 9.1931e-05 | 6.3851 |  | 10.3851 | 4 | 10.3851 | 39.9067 | 19.9534 | 20 | 20 | -0.046643 | -0.58478
1974 | 32.9 | 1.9999 | 10.3996 | 2 | 10.4 | 39.9074 | 0 | 0.00038141 | 127.679 | 3.0422e-05 | 0.0011442 | 6.3839 | 9.1266e-05 | 6.3852 |  | 10.3852 | 4 | 10.3852 | 39.9074 | 19.9537 | 20 | 20 | -0.0463 | -0.63108
1975 | 32.9167 | 1.9999 | 10.3996 | 2 | 10.4 | 39.9081 | 0 | 0.00041161 | 127.6794 | 3.0198e-05 | 0.0012348 | 6.384 | 9.0595e-05 | 6.3853 |  | 10.3853 | 4 | 10.3853 | 39.9081 | 19.954 | 20 | 20 | -0.045955 | -0.67704
1976 | 32.9333 | 1.9999 | 10.3996 | 2 | 10.4 | 39.9088 | 0 | 0.00044158 | 127.6798 | 2.9973e-05 | 0.0013248 | 6.384 | 8.992e-05 | 6.3854 |  | 10.3854 | 4 | 10.3854 | 39.9088 | 19.9544 | 20 | 20 | -0.045607 | -0.72265
1977 | 32.95 | 1.9999 | 10.3995 | 2 | 10.4 | 39.9095 | 0 | 0.00047133 | 127.6803 | 2.9746e-05 | 0.001414 | 6.384 | 8.9239e-05 | 6.3855 |  | 10.3855 | 4 | 10.3855 | 39.9095 | 19.9547 | 20 | 20 | -0.045257 | -0.7679
1978 | 32.9667 | 1.9998 | 10.3995 | 2 | 10.4 | 39.9102 | 0 | 0.00050085 | 127.6808 | 2.9518e-05 | 0.0015025 | 6.384 | 8.8553e-05 | 6.3856 |  | 10.3856 | 4 | 10.3856 | 39.9102 | 19.9551 | 20 | 20 | -0.044904 | -0.81281
1979 | 32.9833 | 1.9998 | 10.3995 | 2 | 10.4 | 39.9109 | 0 | 0.00053014 | 127.6813 | 2.9288e-05 | 0.0015904 | 6.3841 | 8.7863e-05 | 6.3857 |  | 10.3857 | 4 | 10.3857 | 39.9109 | 19.9555 | 20 | 20 | -0.044549 | -0.85735
1980 | 33 | 1.9998 | 10.3994 | 2 | 10.4 | 39.9116 | 0 | 0.00055919 | 127.6819 | 2.9056e-05 | 0.0016776 | 6.3841 | 8.7168e-05 | 6.3859 |  | 10.3859 | 4 | 10.3859 | 39.9116 | 19.9558 | 20 | 20 | -0.044191 | -0.90155
1981 | 33.0167 | 1.9998 | 10.3994 | 2 | 10.4 | 39.9123 | 0 | 0.00058801 | 127.6825 | 2.8823e-05 | 0.001764 | 6.3841 | 8.6468e-05 | 6.386 |  | 10.386 | 4 | 10.386 | 39.9123 | 19.9562 | 20 | 20 | -0.043831 | -0.94538
1982 | 33.0333 | 1.9998 | 10.3994 | 2 | 10.4 | 39.9131 | 0 | 0.0006166 | 127.6831 | 2.8588e-05 | 0.0018498 | 6.3842 | 8.5764e-05 | 6.3861 |  | 10.3861 | 4 | 10.3861 | 39.9131 | 19.9565 | 20 | 20 | -0.043469 | -0.98885
1983 | 33.05 | 1.9998 | 10.3994 | 2 | 10.4 | 39.9138 | 0 | 0.00064495 | 127.6837 | 2.8352e-05 | 0.0019349 | 6.3842 | 8.5055e-05 | 6.3862 |  | 10.3862 | 4 | 10.3862 | 39.9138 | 19.9569 | 20 | 20 | -0.043105 | -1.032
1984 | 33.0667 | 1.9998 | 10.3993 | 2 | 10.4 | 39.9145 | 0 | 0.00067307 | 127.6844 | 2.8114e-05 | 0.0020192 | 6.3842 | 8.4342e-05 | 6.3863 |  | 10.3863 | 4 | 10.3863 | 39.9145 | 19.9573 | 20 | 20 | -0.042738 | -1.0747
1985 | 33.0833 | 1.9998 | 10.3993 | 2 | 10.4 | 39.9153 | 0 | 0.00070094 | 127.6851 | 2.7875e-05 | 0.0021028 | 6.3843 | 8.3625e-05 | 6.3864 |  | 10.3864 | 4 | 10.3864 | 39.9153 | 19.9576 | 20 | 20 | -0.04237 | -1.1171
1986 | 33.1 | 1.9998 | 10.3993 | 2 | 10.4 | 39.916 | 0 | 0.00072858 | 127.6858 | 2.7635e-05 | 0.0021857 | 6.3843 | 8.2904e-05 | 6.3866 |  | 10.3866 | 4 | 10.3866 | 39.916 | 19.958 | 20 | 20 | -0.041999 | -1.1591
1987 | 33.1167 | 1.9998 | 10.3992 | 2 | 10.4 | 39.9167 | 0 | 0.00075597 | 127.6866 | 2.7393e-05 | 0.0022679 | 6.3843 | 8.2179e-05 | 6.3867 |  | 10.3867 | 4 | 10.3867 | 39.9167 | 19.9584 | 20 | 20 | -0.041626 | -1.2007
1988 | 33.1333 | 1.9998 | 10.3992 | 2 | 10.4 | 39.9175 | 0 | 0.00078312 | 127.6874 | 2.715e-05 | 0.0023494 | 6.3844 | 8.145e-05 | 6.3868 |  | 10.3868 | 4 | 10.3868 | 39.9175 | 19.9587 | 20 | 20 | -0.041252 | -1.2419
1989 | 33.15 | 1.9997 | 10.3992 | 2 | 10.4 | 39.9182 | 0 | 0.00081003 | 127.6882 | 2.6906e-05 | 0.0024301 | 6.3844 | 8.0717e-05 | 6.3869 |  | 10.3869 | 4 | 10.3869 | 39.9182 | 19.9591 | 20 | 20 | -0.040875 | -1.2828
1990 | 33.1667 | 1.9997 | 10.3992 | 2 | 10.4 | 39.919 | 0 | 0.00083669 | 127.689 | 2.666e-05 | 0.0025101 | 6.3845 | 7.998e-05 | 6.387 |  | 10.387 | 4 | 10.387 | 39.919 | 19.9595 | 20 | 20 | -0.040497 | -1.3233
1991 | 33.1833 | 1.9997 | 10.3991 | 2 | 10.4 | 39.9198 | 0 | 0.0008631 | 127.6899 | 2.6413e-05 | 0.0025893 | 6.3845 | 7.9239e-05 | 6.3872 |  | 10.3872 | 4 | 10.3872 | 39.9198 | 19.9599 | 20 | 20 | -0.040117 | -1.3634
1992 | 33.2 | 1.9997 | 10.3991 | 2 | 10.4 | 39.9205 | 0 | 0.00088926 | 127.6908 | 2.6165e-05 | 0.0026678 | 6.3845 | 7.8496e-05 | 6.3873 |  | 10.3873 | 4 | 10.3873 | 39.9205 | 19.9603 | 20 | 20 | -0.039735 | -1.4032
1993 | 33.2167 | 1.9997 | 10.3991 | 2 | 10.4 | 39.9213 | 0 | 0.00091518 | 127.6917 | 2.5916e-05 | 0.0027455 | 6.3846 | 7.7748e-05 | 6.3874 |  | 10.3874 | 4 | 10.3874 | 39.9213 | 19.9606 | 20 | 20 | -0.039351 | -1.4425
1994 | 33.2333 | 1.9997 | 10.3991 | 2 | 10.4 | 39.9221 | 0 | 0.00094085 | 127.6926 | 2.5666e-05 | 0.0028225 | 6.3846 | 7.6998e-05 | 6.3875 |  | 10.3875 | 4 | 10.3875 | 39.9221 | 19.961 | 20 | 20 | -0.038966 | -1.4815
1995 | 33.25 | 1.9997 | 10.399 | 2 | 10.4 | 39.9228 | 0 | 0.00096626 | 127.6936 | 2.5415e-05 | 0.0028988 | 6.3847 | 7.6244e-05 | 6.3877 |  | 10.3877 | 4 | 10.3877 | 39.9228 | 19.9614 | 20 | 20 | -0.038579 | -1.5201
1996 | 33.2667 | 1.9997 | 10.399 | 2 | 10.4 | 39.9236 | 0 | 0.00099142 | 127.6946 | 2.5162e-05 | 0.0029743 | 6.3847 | 7.5487e-05 | 6.3878 |  | 10.3878 | 4 | 10.3878 | 39.9236 | 19.9618 | 20 | 20 | -0.03819 | -1.5582
1997 | 33.2833 | 1.9997 | 10.399 | 2 | 10.4 | 39.9244 | 0 | 0.0010163 | 127.6956 | 2.4909e-05 | 0.003049 | 6.3848 | 7.4727e-05 | 6.3879 |  | 10.3879 | 4 | 10.3879 | 39.9244 | 19.9622 | 20 | 20 | -0.0378 | -1.596
1998 | 33.3 | 1.9997 | 10.399 | 2 | 10.4 | 39.9252 | 0 | 0.001041 | 127.6966 | 2.4655e-05 | 0.003123 | 6.3848 | 7.3964e-05 | 6.388 |  | 10.388 | 4 | 10.388 | 39.9252 | 19.9626 | 20 | 20 | -0.037409 | -1.6335
1999 | 33.3167 | 1.9997 | 10.3989 | 2 | 10.4 | 39.926 | 0 | 0.0010654 | 127.6977 | 2.4399e-05 | 0.0031962 | 6.3849 | 7.3198e-05 | 6.3882 |  | 10.3882 | 4 | 10.3882 | 39.926 | 19.963 | 20 | 20 | -0.037016 | -1.6705
2000 | 33.3333 | 1.9997 | 10.3989 | 2 | 10.4 | 39.9268 | 0 | 0.0010895 | 127.6988 | 2.4143e-05 | 0.0032686 | 6.3849 | 7.2429e-05 | 6.3883 |  | 10.3883 | 4 | 10.3883 | 39.9268 | 19.9634 | 20 | 20 | -0.036622 | -1.7071
2001 | 33.35 | 1.9997 | 10.3989 | 2 | 10.4 | 39.9275 | 0 | 0.0011134 | 127.6999 | 2.3886e-05 | 0.0033402 | 6.385 | 7.1658e-05 | 6.3884 |  | 10.3884 | 4 | 10.3884 | 39.9275 | 19.9638 | 20 | 20 | -0.036227 | -1.7433
2002 | 33.3667 | 1.9996 | 10.3989 | 2 | 10.4 | 39.9283 | 0 | 0.001137 | 127.701 | 2.3628e-05 | 0.0034111 | 6.3851 | 7.0884e-05 | 6.3885 |  | 10.3885 | 4 | 10.3885 | 39.9283 | 19.9642 | 20 | 20 | -0.03583 | -1.7791
2003 | 33.3833 | 1.9996 | 10.3988 | 2 | 10.4 | 39.9291 | 0 | 0.0011604 | 127.7022 | 2.3369e-05 | 0.0034812 | 6.3851 | 7.0108e-05 | 6.3887 |  | 10.3887 | 4 | 10.3887 | 39.9291 | 19.9646 | 20 | 20 | -0.035432 | -1.8146
2004 | 33.4 | 1.9996 | 10.3988 | 2 | 10.4 | 39.9299 | 0 | 0.0011835 | 127.7034 | 2.311e-05 | 0.0035506 | 6.3852 | 6.9329e-05 | 6.3888 |  | 10.3888 | 4 | 10.3888 | 39.9299 | 19.965 | 20 | 20 | -0.035033 | -1.8496
2005 | 33.4167 | 1.9996 | 10.3988 | 2 | 10.4 | 39.9307 | 0 | 0.0012064 | 127.7046 | 2.2849e-05 | 0.0036191 | 6.3852 | 6.8548e-05 | 6.3889 |  | 10.3889 | 4 | 10.3889 | 39.9307 | 19.9654 | 20 | 20 | -0.034632 | -1.8842
2006 | 33.4333 | 1.9996 | 10.3988 | 2 | 10.4 | 39.9315 | 0 | 0.001229 | 127.7058 | 2.2588e-05 | 0.0036869 | 6.3853 | 6.7765e-05 | 6.389 |  | 10.389 | 4 | 10.389 | 39.9315 | 19.9658 | 20 | 20 | -0.034231 | -1.9185
2007 | 33.45 | 1.9996 | 10.3987 | 2 | 10.4 | 39.9323 | 0 | 0.0012513 | 127.7071 | 2.2327e-05 | 0.0037539 | 6.3854 | 6.698e-05 | 6.3892 |  | 10.3892 | 4 | 10.3892 | 39.9323 | 19.9662 | 20 | 20 | -0.033829 | -1.9523
2008 | 33.4667 | 1.9996 | 10.3987 | 2 | 10.4 | 39.9331 | 0 | 0.0012734 | 127.7084 | 2.2064e-05 | 0.0038201 | 6.3854 | 6.6192e-05 | 6.3893 |  | 10.3893 | 4 | 10.3893 | 39.9331 | 19.9666 | 20 | 20 | -0.033425 | -1.9857
2009 | 33.4833 | 1.9996 | 10.3987 | 2 | 10.4 | 39.934 | 0 | 0.0012952 | 127.7096 | 2.1801e-05 | 0.0038855 | 6.3855 | 6.5403e-05 | 6.3894 |  | 10.3894 | 4 | 10.3894 | 39.934 | 19.967 | 20 | 20 | -0.033021 | -2.0188
2010 | 33.5 | 1.9996 | 10.3987 | 2 | 10.4 | 39.9348 | 0 | 0.0013167 | 127.711 | 2.1537e-05 | 0.0039501 | 6.3855 | 6.4612e-05 | 6.3896 |  | 10.3896 | 4 | 10.3896 | 39.9348 | 19.9674 | 20 | 20 | -0.032616 | -2.0514
2011 | 33.5167 | 1.9996 | 10.3987 | 2 | 10.4 | 39.9356 | 0 | 0.001338 | 127.7123 | 2.1273e-05 | 0.0040139 | 6.3856 | 6.3819e-05 | 6.3897 |  | 10.3897 | 4 | 10.3897 | 39.9356 | 19.9678 | 20 | 20 | -0.03221 | -2.0836
2012 | 33.5333 | 1.9996 | 10.3986 | 2 | 10.4 | 39.9364 | 0 | 0.001359 | 127.7137 | 2.1008e-05 | 0.0040769 | 6.3857 | 6.3025e-05 | 6.3898 |  | 10.3898 | 4 | 10.3898 | 39.9364 | 19.9682 | 20 | 20 | -0.031803 | -2.1154
2013 | 33.55 | 1.9996 | 10.3986 | 2 | 10.4 | 39.9372 | 0 | 0.0013797 | 127.715 | 2.0743e-05 | 0.0041391 | 6.3858 | 6.2229e-05 | 6.39 |  | 10.39 | 4 | 10.39 | 39.9372 | 19.9686 | 20 | 20 | -0.031396 | -2.1468
2014 | 33.5667 | 1.9996 | 10.3986 | 2 | 10.4 | 39.938 | 0 | 0.0014002 | 127.7164 | 2.0477e-05 | 0.0042006 | 6.3858 | 6.1431e-05 | 6.3901 |  | 10.3901 | 4 | 10.3901 | 39.938 | 19.969 | 20 | 20 | -0.030987 | -2.1778
2015 | 33.5833 | 1.9996 | 10.3986 | 2 | 10.4 | 39.9388 | 0 | 0.0014204 | 127.7179 | 2.0211e-05 | 0.0042612 | 6.3859 | 6.0632e-05 | 6.3902 |  | 10.3902 | 4 | 10.3902 | 39.9388 | 19.9694 | 20 | 20 | -0.030578 | -2.2083
2016 | 33.6 | 1.9995 | 10.3986 | 2 | 10.4 | 39.9397 | 0 | 0.0014403 | 127.7193 | 1.9944e-05 | 0.004321 | 6.386 | 5.9832e-05 | 6.3903 |  | 10.3903 | 4 | 10.3903 | 39.9397 | 19.9698 | 20 | 20 | -0.030169 | -2.2385
2017 | 33.6167 | 1.9995 | 10.3985 | 2 | 10.4 | 39.9405 | 0 | 0.00146 | 127.7208 | 1.9677e-05 | 0.0043801 | 6.386 | 5.9031e-05 | 6.3905 |  | 10.3905 | 4 | 10.3905 | 39.9405 | 19.9702 | 20 | 20 | -0.029759 | -2.2683
2018 | 33.6333 | 1.9995 | 10.3985 | 2 | 10.4 | 39.9413 | 0 | 0.0014794 | 127.7222 | 1.941e-05 | 0.0044383 | 6.3861 | 5.8229e-05 | 6.3906 |  | 10.3906 | 4 | 10.3906 | 39.9413 | 19.9707 | 20 | 20 | -0.029348 | -2.2976
2019 | 33.65 | 1.9995 | 10.3985 | 2 | 10.4 | 39.9421 | 0 | 0.0014986 | 127.7237 | 1.9142e-05 | 0.0044957 | 6.3862 | 5.7425e-05 | 6.3907 |  | 10.3907 | 4 | 10.3907 | 39.9421 | 19.9711 | 20 | 20 | -0.028937 | -2.3266
2020 | 33.6667 | 1.9995 | 10.3985 | 2 | 10.4 | 39.9429 | 0 | 0.0015174 | 127.7253 | 1.8874e-05 | 0.0045523 | 6.3863 | 5.6621e-05 | 6.3909 |  | 10.3909 | 4 | 10.3909 | 39.9429 | 19.9715 | 20 | 20 | -0.028525 | -2.3551
2021 | 33.6833 | 1.9995 | 10.3985 | 2 | 10.4 | 39.9438 | 0 | 0.0015361 | 127.7268 | 1.8605e-05 | 0.0046082 | 6.3863 | 5.5815e-05 | 6.391 |  | 10.391 | 4 | 10.391 | 39.9438 | 19.9719 | 20 | 20 | -0.028114 | -2.3832
2022 | 33.7 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9446 | 0 | 0.0015544 | 127.7283 | 1.8336e-05 | 0.0046632 | 6.3864 | 5.5009e-05 | 6.3911 |  | 10.3911 | 4 | 10.3911 | 39.9446 | 19.9723 | 20 | 20 | -0.027701 | -2.4109
2023 | 33.7167 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9454 | 0 | 0.0015725 | 127.7299 | 1.8068e-05 | 0.0047174 | 6.3865 | 5.4203e-05 | 6.3913 |  | 10.3913 | 4 | 10.3913 | 39.9454 | 19.9727 | 20 | 20 | -0.027289 | -2.4382
2024 | 33.7333 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9462 | 0 | 0.0015903 | 127.7315 | 1.7799e-05 | 0.0047708 | 6.3866 | 5.3396e-05 | 6.3914 |  | 10.3914 | 4 | 10.3914 | 39.9462 | 19.9731 | 20 | 20 | -0.026876 | -2.4651
2025 | 33.75 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9471 | 0 | 0.0016078 | 127.7331 | 1.7529e-05 | 0.0048234 | 6.3867 | 5.2588e-05 | 6.3915 |  | 10.3915 | 4 | 10.3915 | 39.9471 | 19.9735 | 20 | 20 | -0.026463 | -2.4915
2026 | 33.7667 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9479 | 0 | 0.001625 | 127.7347 | 1.726e-05 | 0.0048751 | 6.3867 | 5.178e-05 | 6.3917 |  | 10.3917 | 4 | 10.3917 | 39.9479 | 19.974 | 20 | 20 | -0.02605 | -2.5176
2027 | 33.7833 | 1.9995 | 10.3984 | 2 | 10.4 | 39.9487 | 0 | 0.001642 | 127.7364 | 1.699e-05 | 0.0049261 | 6.3868 | 5.0971e-05 | 6.3918 |  | 10.3918 | 4 | 10.3918 | 39.9487 | 19.9744 | 20 | 20 | -0.025636 | -2.5432
2028 | 33.8 | 1.9995 | 10.3983 | 2 | 10.4 | 39.9496 | 0 | 0.0016588 | 127.738 | 1.6721e-05 | 0.0049763 | 6.3869 | 5.0162e-05 | 6.3919 |  | 10.3919 | 4 | 10.3919 | 39.9496 | 19.9748 | 20 | 20 | -0.025223 | -2.5684
2029 | 33.8167 | 1.9995 | 10.3983 | 2 | 10.4 | 39.9504 | 0 | 0.0016752 | 127.7397 | 1.6451e-05 | 0.0050256 | 6.387 | 4.9353e-05 | 6.3921 |  | 10.3921 | 4 | 10.3921 | 39.9504 | 19.9752 | 20 | 20 | -0.02481 | -2.5932
2030 | 33.8333 | 1.9995 | 10.3983 | 2 | 10.4 | 39.9512 | 0 | 0.0016914 | 127.7414 | 1.6181e-05 | 0.0050742 | 6.3871 | 4.8544e-05 | 6.3922 |  | 10.3922 | 4 | 10.3922 | 39.9512 | 19.9756 | 20 | 20 | -0.024396 | -2.6176
2031 | 33.85 | 1.9995 | 10.3983 | 2 | 10.4 | 39.952 | 0 | 0.0017073 | 127.7431 | 1.5912e-05 | 0.0051219 | 6.3872 | 4.7735e-05 | 6.3923 |  | 10.3923 | 4 | 10.3923 | 39.952 | 19.976 | 20 | 20 | -0.023983 | -2.6416
2032 | 33.8667 | 1.9995 | 10.3983 | 2 | 10.4 | 39.9529 | 0 | 0.0017229 | 127.7448 | 1.5642e-05 | 0.0051688 | 6.3872 | 4.6927e-05 | 6.3925 |  | 10.3925 | 4 | 10.3925 | 39.9529 | 19.9764 | 20 | 20 | -0.023569 | -2.6652
2033 | 33.8833 | 1.9995 | 10.3983 | 2 | 10.4 | 39.9537 | 0 | 0.0017383 | 127.7466 | 1.5373e-05 | 0.0052149 | 6.3873 | 4.6118e-05 | 6.3926 |  | 10.3926 | 4 | 10.3926 | 39.9537 | 19.9768 | 20 | 20 | -0.023156 | -2.6883
2034 | 33.9 | 1.9995 | 10.3982 | 2 | 10.4 | 39.9545 | 0 | 0.0017534 | 127.7483 | 1.5103e-05 | 0.0052603 | 6.3874 | 4.5309e-05 | 6.3927 |  | 10.3927 | 4 | 10.3927 | 39.9545 | 19.9773 | 20 | 20 | -0.022743 | -2.7111
2035 | 33.9167 | 1.9994 | 10.3982 | 2 | 10.4 | 39.9553 | 0 | 0.0017683 | 127.7501 | 1.4834e-05 | 0.0053048 | 6.3875 | 4.4501e-05 | 6.3929 |  | 10.3929 | 4 | 10.3929 | 39.9553 | 19.9777 | 20 | 20 | -0.02233 | -2.7334
2036 | 33.9333 | 1.9994 | 10.3982 | 2 | 10.4 | 39.9562 | 0 | 0.0017828 | 127.7519 | 1.4564e-05 | 0.0053484 | 6.3876 | 4.3693e-05 | 6.393 |  | 10.393 | 4 | 10.393 | 39.9562 | 19.9781 | 20 | 20 | -0.021918 | -2.7553
2037 | 33.95 | 1.9994 | 10.3982 | 2 | 10.4 | 39.957 | 0 | 0.0017971 | 127.7537 | 1.4295e-05 | 0.0053913 | 6.3877 | 4.2886e-05 | 6.3931 |  | 10.3931 | 4 | 10.3931 | 39.957 | 19.9785 | 20 | 20 | -0.021505 | -2.7768
2038 | 33.9667 | 1.9994 | 10.3982 | 2 | 10.4 | 39.9578 | 0 | 0.0018111 | 127.7555 | 1.4026e-05 | 0.0054334 | 6.3878 | 4.2079e-05 | 6.3933 |  | 10.3933 | 4 | 10.3933 | 39.9578 | 19.9789 | 20 | 20 | -0.021093 | -2.7979
2039 | 33.9833 | 1.9994 | 10.3982 | 2 | 10.4 | 39.9586 | 0 | 0.0018249 | 127.7573 | 1.3758e-05 | 0.0054747 | 6.3879 | 4.1273e-05 | 6.3934 |  | 10.3934 | 4 | 10.3934 | 39.9586 | 19.9793 | 20 | 20 | -0.020682 | -2.8186
2040 | 34 | 1.9994 | 10.3982 | 2 | 10.4 | 39.9595 | 0 | 0.0018384 | 127.7592 | 1.3489e-05 | 0.0055152 | 6.388 | 4.0468e-05 | 6.3935 |  | 10.3935 | 4 | 10.3935 | 39.9595 | 19.9797 | 20 | 20 | -0.020271 | -2.8389
2041 | 34.0167 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9603 | 0 | 0.0018516 | 127.761 | 1.3221e-05 | 0.0055548 | 6.3881 | 3.9663e-05 | 6.3936 |  | 10.3936 | 4 | 10.3936 | 39.9603 | 19.9801 | 20 | 20 | -0.01986 | -2.8587
2042 | 34.0333 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9611 | 0 | 0.0018646 | 127.7629 | 1.2953e-05 | 0.0055937 | 6.3881 | 3.886e-05 | 6.3938 |  | 10.3938 | 4 | 10.3938 | 39.9611 | 19.9806 | 20 | 20 | -0.01945 | -2.8782
2043 | 34.05 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9619 | 0 | 0.0018772 | 127.7647 | 1.2686e-05 | 0.0056317 | 6.3882 | 3.8057e-05 | 6.3939 |  | 10.3939 | 4 | 10.3939 | 39.9619 | 19.981 | 20 | 20 | -0.01904 | -2.8972
2044 | 34.0667 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9627 | 0 | 0.0018897 | 127.7666 | 1.2418e-05 | 0.005669 | 6.3883 | 3.7255e-05 | 6.394 |  | 10.394 | 4 | 10.394 | 39.9627 | 19.9814 | 20 | 20 | -0.018631 | -2.9159
2045 | 34.0833 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9636 | 0 | 0.0019018 | 127.7685 | 1.2151e-05 | 0.0057054 | 6.3884 | 3.6454e-05 | 6.3942 |  | 10.3942 | 4 | 10.3942 | 39.9636 | 19.9818 | 20 | 20 | -0.018222 | -2.9341
2046 | 34.1 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9644 | 0 | 0.0019137 | 127.7705 | 1.1885e-05 | 0.0057411 | 6.3885 | 3.5655e-05 | 6.3943 |  | 10.3943 | 4 | 10.3943 | 39.9644 | 19.9822 | 20 | 20 | -0.017814 | -2.9519
2047 | 34.1167 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9652 | 0 | 0.0019253 | 127.7724 | 1.1619e-05 | 0.005776 | 6.3886 | 3.4857e-05 | 6.3944 |  | 10.3944 | 4 | 10.3944 | 39.9652 | 19.9826 | 20 | 20 | -0.017407 | -2.9693
2048 | 34.1333 | 1.9994 | 10.3981 | 2 | 10.4 | 39.966 | 0 | 0.0019367 | 127.7743 | 1.1353e-05 | 0.00581 | 6.3887 | 3.406e-05 | 6.3946 |  | 10.3946 | 4 | 10.3946 | 39.966 | 19.983 | 20 | 20 | -0.017 | -2.9863
2049 | 34.15 | 1.9994 | 10.3981 | 2 | 10.4 | 39.9668 | 0 | 0.0019478 | 127.7763 | 1.1088e-05 | 0.0058433 | 6.3888 | 3.3264e-05 | 6.3947 |  | 10.3947 | 4 | 10.3947 | 39.9668 | 19.9834 | 20 | 20 | -0.016595 | -3.0029
2050 | 34.1667 | 1.9994 | 10.398 | 2 | 10.4 | 39.9676 | 0 | 0.0019586 | 127.7782 | 1.0823e-05 | 0.0058757 | 6.3889 | 3.247e-05 | 6.3948 |  | 10.3948 | 4 | 10.3948 | 39.9676 | 19.9838 | 20 | 20 | -0.01619 | -3.0191
2051 | 34.1833 | 1.9994 | 10.398 | 2 | 10.4 | 39.9684 | 0 | 0.0019691 | 127.7802 | 1.0559e-05 | 0.0059074 | 6.389 | 3.1678e-05 | 6.3949 |  | 10.3949 | 4 | 10.3949 | 39.9684 | 19.9842 | 20 | 20 | -0.015785 | -3.0349
2052 | 34.2 | 1.9994 | 10.398 | 2 | 10.4 | 39.9692 | 0 | 0.0019794 | 127.7822 | 1.0296e-05 | 0.0059383 | 6.3891 | 3.0887e-05 | 6.3951 |  | 10.3951 | 4 | 10.3951 | 39.9692 | 19.9846 | 20 | 20 | -0.015382 | -3.0503
2053 | 34.2167 | 1.9994 | 10.398 | 2 | 10.4 | 39.97 | 0 | 0.0019895 | 127.7842 | 1.0033e-05 | 0.0059684 | 6.3892 | 3.0098e-05 | 6.3952 |  | 10.3952 | 4 | 10.3952 | 39.97 | 19.985 | 20 | 20 | -0.01498 | -3.0652
2054 | 34.2333 | 1.9994 | 10.398 | 2 | 10.4 | 39.9708 | 0 | 0.0019992 | 127.7862 | 9.7701e-06 | 0.0059977 | 6.3893 | 2.931e-05 | 6.3953 |  | 10.3953 | 4 | 10.3953 | 39.9708 | 19.9854 | 20 | 20 | -0.014578 | -3.0798
2055 | 34.25 | 1.9994 | 10.398 | 2 | 10.4 | 39.9716 | 0 | 0.0020087 | 127.7882 | 9.5082e-06 | 0.0060262 | 6.3894 | 2.8525e-05 | 6.3955 |  | 10.3955 | 4 | 10.3955 | 39.9716 | 19.9858 | 20 | 20 | -0.014177 | -3.094
2056 | 34.2667 | 1.9994 | 10.398 | 2 | 10.4 | 39.9724 | 0 | 0.002018 | 127.7902 | 9.247e-06 | 0.006054 | 6.3895 | 2.7741e-05 | 6.3956 |  | 10.3956 | 4 | 10.3956 | 39.9724 | 19.9862 | 20 | 20 | -0.013778 | -3.1078
2057 | 34.2833 | 1.9994 | 10.398 | 2 | 10.4 | 39.9732 | 0 | 0.002027 | 127.7922 | 8.9864e-06 | 0.0060809 | 6.3896 | 2.6959e-05 | 6.3957 |  | 10.3957 | 4 | 10.3957 | 39.9732 | 19.9866 | 20 | 20 | -0.013379 | -3.1212
2058 | 34.3 | 1.9994 | 10.398 | 2 | 10.4 | 39.974 | 0 | 0.0020357 | 127.7942 | 8.7265e-06 | 0.0061071 | 6.3897 | 2.6179e-05 | 6.3958 |  | 10.3958 | 4 | 10.3958 | 39.974 | 19.987 | 20 | 20 | -0.012982 | -3.1341
2059 | 34.3167 | 1.9994 | 10.398 | 2 | 10.4 | 39.9748 | 0 | 0.0020442 | 127.7963 | 8.4672e-06 | 0.0061325 | 6.3898 | 2.5402e-05 | 6.396 |  | 10.396 | 4 | 10.396 | 39.9748 | 19.9874 | 20 | 20 | -0.012586 | -3.1467
2060 | 34.3333 | 1.9994 | 10.3979 | 2 | 10.4 | 39.9756 | 0 | 0.0020524 | 127.7983 | 8.2087e-06 | 0.0061572 | 6.3899 | 2.4626e-05 | 6.3961 |  | 10.3961 | 4 | 10.3961 | 39.9756 | 19.9878 | 20 | 20 | -0.01219 | -3.1589
2061 | 34.35 | 1.9994 | 10.3979 | 2 | 10.4 | 39.9764 | 0 | 0.0020603 | 127.8004 | 7.9509e-06 | 0.006181 | 6.39 | 2.3853e-05 | 6.3962 |  | 10.3962 | 4 | 10.3962 | 39.9764 | 19.9882 | 20 | 20 | -0.011796 | -3.1707
2062 | 34.3667 | 1.9994 | 10.3979 | 2 | 10.4 | 39.9772 | 0 | 0.002068 | 127.8025 | 7.6939e-06 | 0.0062041 | 6.3901 | 2.3082e-05 | 6.3964 |  | 10.3964 | 4 | 10.3964 | 39.9772 | 19.9886 | 20 | 20 | -0.011403 | -3.1821
2063 | 34.3833 | 1.9994 | 10.3979 | 2 | 10.4 | 39.978 | 0 | 0.0020755 | 127.8045 | 7.4377e-06 | 0.0062264 | 6.3902 | 2.2313e-05 | 6.3965 |  | 10.3965 | 4 | 10.3965 | 39.978 | 19.989 | 20 | 20 | -0.011012 | -3.1931
2064 | 34.4 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9788 | 0 | 0.0020826 | 127.8066 | 7.1823e-06 | 0.0062479 | 6.3903 | 2.1547e-05 | 6.3966 |  | 10.3966 | 4 | 10.3966 | 39.9788 | 19.9894 | 20 | 20 | -0.010622 | -3.2037
2065 | 34.4167 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9795 | 0 | 0.0020896 | 127.8087 | 6.9277e-06 | 0.0062687 | 6.3904 | 2.0783e-05 | 6.3967 |  | 10.3967 | 4 | 10.3967 | 39.9795 | 19.9898 | 20 | 20 | -0.010232 | -3.214
2066 | 34.4333 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9803 | 0 | 0.0020963 | 127.8108 | 6.6739e-06 | 0.0062888 | 6.3905 | 2.0022e-05 | 6.3968 |  | 10.3968 | 4 | 10.3968 | 39.9803 | 19.9902 | 20 | 20 | -0.0098447 | -3.2238
2067 | 34.45 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9811 | 0 | 0.0021027 | 127.8129 | 6.421e-06 | 0.006308 | 6.3906 | 1.9263e-05 | 6.397 |  | 10.397 | 4 | 10.397 | 39.9811 | 19.9905 | 20 | 20 | -0.0094584 | -3.2333
2068 | 34.4667 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9819 | 0 | 0.0021088 | 127.815 | 6.169e-06 | 0.0063265 | 6.3908 | 1.8507e-05 | 6.3971 |  | 10.3971 | 4 | 10.3971 | 39.9819 | 19.9909 | 20 | 20 | -0.0090734 | -3.2424
2069 | 34.4833 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9826 | 0 | 0.0021148 | 127.8171 | 5.9179e-06 | 0.0063443 | 6.3909 | 1.7754e-05 | 6.3972 |  | 10.3972 | 4 | 10.3972 | 39.9826 | 19.9913 | 20 | 20 | -0.0086898 | -3.251
2070 | 34.5 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9834 | 0 | 0.0021204 | 127.8193 | 5.6678e-06 | 0.0063613 | 6.391 | 1.7003e-05 | 6.3973 |  | 10.3973 | 4 | 10.3973 | 39.9834 | 19.9917 | 20 | 20 | -0.0083077 | -3.2594
2071 | 34.5167 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9841 | 0 | 0.0021258 | 127.8214 | 5.4185e-06 | 0.0063775 | 6.3911 | 1.6256e-05 | 6.3975 |  | 10.3975 | 4 | 10.3975 | 39.9841 | 19.9921 | 20 | 20 | -0.0079271 | -3.2673
2072 | 34.5333 | 1.9993 | 10.3979 | 2 | 10.4 | 39.9849 | 0 | 0.002131 | 127.8235 | 5.1703e-06 | 0.006393 | 6.3912 | 1.5511e-05 | 6.3976 |  | 10.3976 | 4 | 10.3976 | 39.9849 | 19.9925 | 20 | 20 | -0.007548 | -3.2748
CONTROL LEVEL SIMULATION
CONTROLLER
PROCESS
∑24_(𝑖=0)^𝑡▒(𝐸_𝑖 )
𝐸_𝑖
𝐸_𝑖−𝐸_(𝑖−1)
Fin, mc/h
Fout, mc/h
CYLINDRICAL TANK